## Lines
|  |  | Substation_1 | Substation_2 |  | MaximumCurrentImax(A) | [6 empty] | Dynamiclinerating(DLR) |  | Electrical Parameters
NE_name | EIC_Code | TSO | Full_name | Full_name | Voltage_level(kV) | Period1 | Period2 | Period3 | Period4 | Period5 | Period6 | Fixed | DLRmin(A) | DLRmax(A) | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B(μS) | Length_(km) | Comment
Eula - Röhrsdorf 203 | 11TD8L203------C | 50HERTZ | Eula | Röhrsdorf | 220 | MaximumCurrentImax(A) Period1: 790 |  |  |  | 4.0937 | 18.349 | 161.1637 | 51.511
Röhrsdorf - Weida 207 | 11TD8L207------H | 50HERTZ | Röhrsdorf | Weida | 220 | MaximumCurrentImax(A) Period1: 790 |  |  |  | 7.5895 | 31.888 | 348.7168 | 98.324
Eula - Weida 208 | 11TD8L208------9 | 50HERTZ | Eula | Weida | 220 | MaximumCurrentImax(A) Period1: 1070 |  |  |  | 5.0537 | 19.541 | 264.2394 | 67.55
Bentwisch - Güstrow 275 | 11TD8L275------7 | 50HERTZ | Bentwisch | Güstrow | 220 | MaximumCurrentImax(A) Period1: 1200 |  |  |  | 1.909 | 12.055 | 158.0849 | 41.418
Wuhlheide - Thyrow 291 | 11TD8L291------L | 50HERTZ | Wuhlheide | Thyrow | 220 | MaximumCurrentImax(A) Period1: 960 |  |  |  | 2.9672 | 11.191 | 266.784 | 38.882
Hennigsdorf - Wustermark 295 | 11TD8L295------Q | 50HERTZ | Hennigsdorf | Wustermark | 220 | MaximumCurrentImax(A) Period1: 1070 |  |  |  | 0.548 | 6.85 | 129.1195 | 27.4
Marzahn - Wuhlheide 301 | 11TD8L301------I | 50HERTZ | Marzahn | Wuhlheide | 220 | MaximumCurrentImax(A) Period1: 1070 |  |  |  | 0.5487 | 2.4908 | 37.0708 | 9.111
Marzahn - Wuhlheide(Abzweig) 302/1 | 11TD8L302------A | 50HERTZ | Marzahn | Wuhlheide (Abzweig) | 220 | MaximumCurrentImax(A) Period1: 960 |  |  |  | 0.545 | 2.4772 | 37.0708 | 9.111
Wuhlheide (Abzweig) - Thyrow 302/2 | 11TD8L302------A | 50HERTZ | Wuhlheide (Abzweig) | Thyrow | 220 | MaximumCurrentImax(A) Period1: 960 |  |  |  | 2.9672 | 11.191 | 153.1212 | 38.882
Bertikow - Neuenhagen303 | 11TD8L303------2 | 50HERTZ | Bertikow | Neuenhagen | 220 | MaximumCurrentImax(A) Period1: 1070 |  |  |  | 6.6733 | 25.638 | 321.165 | 86.064
Neuenhagen - Vierraden 304 | 11TD8L304------V | 50HERTZ | Neuenhagen | Vierraden | 220 | MaximumCurrentImax(A) Period1: 1070 |  |  |  | 7.9376 | 29.701 | 375.9858 | 100.756
Bertikow - Pasewalk 305 | 11TD8L305------N | 50HERTZ | Bertikow | Pasewalk | 220 | MaximumCurrentImax(A) Period1: 900 |  |  |  | 2.2852 | 8.7795 | 109.9872 | 29.471
Vierraden - Pasewalk 306 | 11TD8L306------F | 50HERTZ | Vierraden | Pasewalk | 220 | MaximumCurrentImax(A) Period1: 1070 |  |  |  | 4.9243 | 18.121 | 230.9071 | 61.885
Lubmin - Lüdershagen 313 | 11TD8L313------U | 50HERTZ | Lubmin | Lüdershagen | 220 | MaximumCurrentImax(A) Period1: 1200 |  |  |  | 2.821 | 16.33 | 214.3823 | 56.212
Lubmin - Lüdershagen 314 | 11TD8L314------M | 50HERTZ | Lubmin | Lüdershagen | 220 | MaximumCurrentImax(A) Period1: 1200 |  |  |  | 2.821 | 16.33 | 214.3823 | 56.212
Pasewalk - Güstrow 315 | 11TD8L315------E | 50HERTZ | Pasewalk | Güstrow | 220 | MaximumCurrentImax(A) Period1: 900 |  |  |  | 12.1223 | 44.3118 | 572.3982 | 151.143
Pasewalk - Güstrow 316 | 11TD8L316------6 | 50HERTZ | Pasewalk | Güstrow | 220 | MaximumCurrentImax(A) Period1: 900 |  |  |  | 12.1223 | 44.3118 | 572.3982 | 151.143
Lüdershagen - Güstrow 317-276 | 11TD8L317-276--N | 50HERTZ | Lüdershagen | Güstrow | 220 | MaximumCurrentImax(A) Period1: 1200 |  |  |  | 6.59 | 31.384 | 404.4486 | 106.538
Lüdershagen - Bentwisch 318 | 11TD8L318------R | 50HERTZ | Lüdershagen | Bentwisch | 220 | MaximumCurrentImax(A) Period1: 1200 |  |  |  | 4.69 | 19.401 | 247.3376 | 65.349
Parchim/Süd - Güstrow 328 | 11TD8L328------I | 50HERTZ | Parchim/Süd | Güstrow | 220 | MaximumCurrentImax(A) Period1: 900 |  |  |  | 15.5033 | 57.559 | 196.2239 | 52.317
Parchim/Süd - Wolmirstedt 332-322 | 11TD8L332-322--6 | 50HERTZ | Parchim/Süd | Wolmirstedt | 220 | MaximumCurrentImax(A) Period1: 900 |  |  |  | 9.6255 | 40.6047 | 582.1371 | 141.507
Eula - Wolkramshausen 357 | 11TD8L357-----0Y | 50HERTZ | Eula | Wolkramshausen | 220 | MaximumCurrentImax(A) Period1: 1070 |  |  |  | 12.208 | 46.854 | 600.0442 | 159.147
Eula - Wolkramshausen 358 | 11TD8L358------S | 50HERTZ | Eula | Wolkramshausen | 220 | MaximumCurrentImax(A) Period1: 1070 |  |  |  | 12.208 | 46.854 | 600.0442 | 159.147
Vieselbach - Wolkramshausen 367 | 11TD8L367------R | 50HERTZ | Vieselbach | Wolkramshausen | 220 | MaximumCurrentImax(A) Period1: 1600 |  |  |  | 2.5437 | 19.586 | 245.6725 | 65.756
Vieselbach - Wolkramshausen 368 | 11TD8L368------J | 50HERTZ | Vieselbach | Wolkramshausen | 220 | MaximumCurrentImax(A) Period1: 1600 |  |  |  | 2.5437 | 19.586 | 245.6725 | 65.756
Vieselbach - Remptendorf - Großschwabhausen 415 | 11TD8L415------4 | 50HERTZ | Vieselbach | Remptendorf - Großschwabhausen | 400 | MaximumCurrentImax(A) Period1: 2720 |  |  |  | 3.004 | 19.631 | 338.0982 | 77.547
Vieselbach - Remptendorf 416 | 11TD8L416------X | 50HERTZ | Vieselbach | Remptendorf | 400 | MaximumCurrentImax(A) Period1: 2720 |  |  |  | 3.0161 | 19.711 | 339.5433 | 77.547
Krümmel - Görries 419 | 11TD8L419------9 | 50HERTZ | Krümmel | Görries | 400 | MaximumCurrentImax(A) Period1: 2700 |  |  |  | 2.2112 | 22.407 | 389.0863 | 87.47
Krümmel - Wessin 420 | 11TD8L420------Z | 50HERTZ | Krümmel | Wessin | 400 | MaximumCurrentImax(A) Period1: 2700 |  |  |  | 2.9614 | 28.516 | 495.7119 | 111.421
Görries - Güstrow 423 | 11TD8L423------B | 50HERTZ | Görries | Güstrow | 400 | MaximumCurrentImax(A) Period1: 2720 |  |  |  | 2.2401 | 18.244 | 311.9916 | 71.582
Wessin - Güstrow 424 | 11TD8L424------3 | 50HERTZ | Wessin | Güstrow | 400 | MaximumCurrentImax(A) Period1: 2720 |  |  |  | 1.4741 | 12.006 | 205.2402 | 47.103
Wolmirstedt - Förderstedt 437 | 11TD8L437------7 | 50HERTZ | Wolmirstedt | Förderstedt | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.3442 | 12.79 | 209.554 | 48.545
Wolmirstedt - Förderstedt 438 | 11TD8L438-----0Y | 50HERTZ | Wolmirstedt | Förderstedt | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.3442 | 12.79 | 209.576 | 48.545
Eisenach - Vieselbach 454 | 11TD8L454------D | 50HERTZ | Eisenach | Vieselbach | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.891 | 18.946 | 306.5252 | 72.285
Altenfeld - Remptendorf 463 | 11TD8L463------C | 50HERTZ | Altenfeld | Remptendorf | 400 | MaximumCurrentImax(A) Period1: 2370 |  |  |  | 1.4946 | 13.5377 | 208.5389 | 50.254
Altenfeld - Remptendorf 464 | 11TD8L464------4 | 50HERTZ | Altenfeld | Remptendorf | 400 | MaximumCurrentImax(A) Period1: 2370 |  |  |  | 1.4946 | 13.5377 | 208.5389 | 50.254
Vieselbach - Altenfeld 467 | 11TD8L467------H | 50HERTZ | Vieselbach | Altenfeld | 400 | MaximumCurrentImax(A) Period1: 3600 |  |  |  | 1.1669 | 14.503 | 267.6637 | 56.081
Vieselbach - Altenfeld 468 | 11TD8L468------9 | 50HERTZ | Vieselbach | Altenfeld | 400 | MaximumCurrentImax(A) Period1: 3600 |  |  |  | 1.1669 | 14.503 | 267.6637 | 56.081
Lauchstädt - Vieselbach 471 | 11TD8L471------J | 50HERTZ | Lauchstädt | Vieselbach | 400 | MaximumCurrentImax(A) Period1: 3600 |  |  |  | 1.4276 | 19.656 | 358.456 | 78.069
Lauchstädt - Vieselbach 472 | 11TD8L472------B | 50HERTZ | Lauchstädt | Vieselbach | 400 | MaximumCurrentImax(A) Period1: 3600 |  |  |  | 1.4276 | 19.656 | 361.597 | 78.069
Lubmin - Altentreptow/Nord 475 | 11TD8L475------O | 50HERTZ | Lubmin | Altentreptow/Nord | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.4206 | 13.747 | 219.5659 | 52.115
Lubmin - Altentreptow/Süd 476 | 11T0-0000-0007-7 | 50HERTZ | Lubmin | Altentreptow/Süd | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.622 | 17.826 | 290.2832 | 68.8
Altentreptow/Nord - Altentreptow/Süd 477 | 11T0-0000-0008-4 | 50HERTZ | Altentreptow/Nord | Altentreptow/Süd | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 0.395 | 4.342 | 70.7801 | 16.767
Altentreptow/Süd - Gransee 479 | 11TD8L479------T | 50HERTZ | Altentreptow/Süd | Gransee | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.814 | 19.938 | 325.2491 | 77.008
Stendal/West - Wolmirstedt 487 |  | 50HERTZ | Stendal/West | Wolmirstedt | 400 | MaximumCurrentImax(A) Period1: 3600 |  |  |  | 0.58458 | 9.2916 | 172.4734 | 37.245
Stendal/West - Wolmirstedt 488 | 11T0-0000-0980-P | 50HERTZ | Stendal/West | Wolmirstedt | 400 | MaximumCurrentImax(A) Period1: 3600 |  |  |  | 0.58458 | 9.2916 | 172.4734 | 37.245
Stendal/West - Wolmirstedt 489 | 11TD8L489------K | 50HERTZ | Stendal/West | Wolmirstedt | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.1824 | 9.63 | 160.8181 | 37.245
Stendal/West - Wolmirstedt 490 | 11TD8L490------9 | 50HERTZ | Stendal/West | Wolmirstedt | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.1824 | 9.63 | 160.8181 | 37.245
Wolmirstedt - Teufelsbruch 493 | 11TD8L493------M | 50HERTZ | Wolmirstedt | Teufelsbruch | 400 | MaximumCurrentImax(A) Period1: 2400 |  |  |  | 3.6651 | 33.198 | 518.6769 | 124.397
Wolmirstedt - Wustermark 494 | 11TD8L494------E | 50HERTZ | Wolmirstedt | Wustermark | 400 | MaximumCurrentImax(A) Period1: 2500 |  |  |  | 3.1838 | 27.944 | 434.4194 | 104.103
Neuenhagen - Marzahn 495 | 11TD8L495------6 | 50HERTZ | Neuenhagen | Marzahn | 400 | MaximumCurrentImax(A) Period1: 2280 |  |  |  | 0.7606 | 4.3135 | 71.9425 | 16.937
Neuenhagen - Marzahn 496 | 11TD8L496------Z | 50HERTZ | Neuenhagen | Marzahn | 400 | MaximumCurrentImax(A) Period1: 2400 |  |  |  | 0.7606 | 4.3135 | 71.9425 | 16.937
Wustermark - Teufelsbruch 498 | 11TD8L498------J | 50HERTZ | Wustermark | Teufelsbruch | 400 | MaximumCurrentImax(A) Period1: 2400 |  |  |  | 0.7176 | 7.7358 | 129.8106 | 29.597
Jessen/Nord - Lauchstädt 499 | 11TD8L499------B | 50HERTZ | Jessen/Nord | Lauchstädt | 400 | MaximumCurrentImax(A) Period1: 2040 |  |  |  | 3.3388 | 25.4187 | 464.5787 | 102.157
Jessen/Nord - Marke 500 | 11TD8L500------6 | 50HERTZ | Jessen/Nord | Marke | 400 | MaximumCurrentImax(A) Period1: 2040 |  |  |  | 3.4508 | 26.8854 | 490.5911 | 107.37
Ragow - Schönewalde 501 | 11T0-0000-0040-C | 50HERTZ | Ragow | Schönewalde | 400 | MaximumCurrentImax(A) Period1: 2040 |  |  |  | 1.6985 | 13.4421 | 246.772 | 54.003
Ragow - Jessen/Nord 502 | 11TD8L502-----1N | 50HERTZ | Ragow | Jessen/Nord | 400 | MaximumCurrentImax(A) Period1: 2040 |  |  |  | 1.945 | 15.45 | 290.28 | 61.782
Schönewalde - Jessen/Nord 503 | 11TD8L503-----1F | 50HERTZ | Schönewalde | Jessen/Nord | 400 | MaximumCurrentImax(A) Period1: 2040 |  |  |  | 0.25355 | 2.0615 | 36.2854 | 7.953
Marke - Lauchstädt 504 | 11TD8L504------B | 50HERTZ | Marke | Lauchstädt | 400 | MaximumCurrentImax(A) Period1: 2040 |  |  |  | 2.104 | 12.729 | 230.1531 | 50.873
Lubmin - Siedenbrünzow 509 | 11TD8L509------8 | 50HERTZ | Lubmin | Siedenbrünzow | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.5903 | 14.442 | 243.1279 | 56.205
Lubmin - Siedenbrünzow 510 | 11TD8L510------Y | 50HERTZ | Lubmin | Siedenbrünzow | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.5903 | 14.442 | 243.1279 | 56.205
Siedenbrünzow - Güstrow 512 | 11TD8L512------I | 50HERTZ | Siedenbrünzow | Güstrow | 400 | MaximumCurrentImax(A) Period1: 2500 |  |  |  | 3.3653 | 25.045 | 386.9186 | 93.611
Siedenbrünzow - Putlitz/Süd 513 | 11TD8L513------A | 50HERTZ | Siedenbrünzow | Putlitz/Süd | 400 | MaximumCurrentImax(A) Period1: 2500 |  |  |  | 2.589 | 28.065 | 464.5787 | 109.1
Güstrow - Putlitz/Süd 514 | 11TD8L514-----1Z | 50HERTZ | Güstrow | Putlitz/Süd | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 2.882 | 26.429 | 422.23 | 100.3
Perleberg - Stendal/West 516 | 11TD8L516------N | 50HERTZ | Perleberg | Stendal/West | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 2.4508 | 19.375 | 324.7778 | 75.543
Gransee - Neuenhagen 517 | 11TD8L517-----1B | 50HERTZ | Gransee | Neuenhagen | 400 | MaximumCurrentImax(A) Period1: 2040 |  |  |  | 1.659 | 18.225 | 296.4093 | 70.32
Altentreptow/Süd - Malchow 518 | 11T0-0000-0010-O | 50HERTZ | Altentreptow/Süd | Malchow | 400 | MaximumCurrentImax(A) Period1: 2040 |  |  |  | 3.09 | 33.95 | 553.2345 | 131.262
Neuenhagen - Malchow 520 | 11TD8L520------P | 50HERTZ | Neuenhagen | Malchow | 400 | MaximumCurrentImax(A) Period1: 2040 |  |  |  | 0.5655 | 6.2143 | 101.1279 | 23.992
Wustermark - Ragow 521-525 | 11TD8L521-525--G | 50HERTZ | Wustermark | Ragow | 400 | MaximumCurrentImax(A) Period1: 2504 |  |  |  | 4.0033 | 32.625 | 585.4358 | 130.739
Thyrow - Ragow 522 | 11TD8L522------9 | 50HERTZ | Thyrow | Ragow | 400 | MaximumCurrentImax(A) Period1: 2504 |  |  |  | 1.9479 | 15.382 | 277.9681 | 61.804
Wustermark - Thyrow 526 | 11TD8L526------E | 50HERTZ | Wustermark | Thyrow | 220 | MaximumCurrentImax(A) Period1: 1290 |  |  |  | 2.0631 | 17.306 | 312.5256 | 69.44
Förderstedt - Ragow 531 | 11TD8L531------8 | 50HERTZ | Förderstedt | Ragow | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 4.9858 | 46.695 | 765.6061 | 179.426
Förderstedt - Jessen/Nord 533 | 11T0-0000-0042-6 | 50HERTZ | Förderstedt | Jessen/Nord | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 3.2516 | 30.4911 | 527.0964 | 117.5
Lauchstädt - Wolmirstedt 535 | 11TD8L535------D | 50HERTZ | Lauchstädt | Wolmirstedt | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 5.4291 | 40.6894 | 676.6991 | 155.36
Wolmirstedt - Klostermansfeld 536 | 11TD8L536------5 | 50HERTZ | Wolmirstedt | Klostermansfeld | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 3.8793 | 30.282 | 504.0057 | 117.188
Klostermansfeld - Lauchstädt 538 | 11TD8L538------Q | 50HERTZ | Klostermansfeld | Lauchstädt | 400 | MaximumCurrentImax(A) Period1: 2500 |  |  |  | 1.3812 | 10.0828 | 169.6146 | 38.769
Ragow - Preilack 539 | 11TD8L539------I | 50HERTZ | Ragow | Preilack | 400 | MaximumCurrentImax(A) Period1: 2280 |  |  |  | 1.3485 | 10.826 | 191.5743 | 43.164
Ragow - Preilack 540 | 11TD8L540------7 | 50HERTZ | Ragow | Preilack | 400 | MaximumCurrentImax(A) Period1: 2280 |  |  |  | 1.3485 | 10.826 | 191.5743 | 43.164
Graustein - Preilack 541 | 11TD8L541-----0Y | 50HERTZ | Graustein | Preilack | 400 | MaximumCurrentImax(A) Period1: 2000 |  |  |  | 2.0053 | 15.874 | 269.1402 | 62.459
Graustein - Preilack 542 | 11TD8L542------S | 50HERTZ | Graustein | Preilack | 400 | MaximumCurrentImax(A) Period1: 2000 |  |  |  | 2.0053 | 15.874 | 269.1402 | 62.459
Bentwisch - Güstrow 543 | 11TD8L543------K | 50HERTZ | Bentwisch | Güstrow | 400 | MaximumCurrentImax(A) Period1: 2720 |  |  |  | 0.9146 | 9.0037 | 157.331 | 35.561
Bentwisch - Güstrow 544 | 11TD8L544------C | 50HERTZ | Bentwisch | Güstrow | 400 | MaximumCurrentImax(A) Period1: 2720 |  |  |  | 0.9146 | 9.0037 | 157.331 | 35.561
Eisenhüttenstadt (Abzweig) - Eisenhüttenstadt 547-2 | 11TD8L547------P | 50HERTZ | Eisenhüttenstadt (Abzweig) | Eisenhüttenstadt | 400 | MaximumCurrentImax(A) Period1: 1200 |  |  |  | 0.502 | 1.818 | 34.6204 | 7.526
Eisenhüttenstadt (Abzweig) - Preilack 547-1 | 11TD8L547------P | 50HERTZ | Eisenhüttenstadt (Abzweig) | Preilack | 400 | MaximumCurrentImax(A) Period1: 2280 |  |  |  | 1.422 | 9.63 | 170.8712 | 38.476
Neuenhagen - Heinersdorf (Abzweig) 547-3 | 11TD8L547------P | 50HERTZ | Neuenhagen | Heinersdorf (Abzweig) | 400 | MaximumCurrentImax(A) Period1: 2504 |  |  |  | 1.543 | 10.452 | 185.1026 | 41.722
Eisenhüttenstadt (Abzweig) - Heinersdorf (Abzweig) 547-4 | 11TD8L547------P | 50HERTZ | Eisenhüttenstadt (Abzweig) | Heinersdorf (Abzweig) | 400 | MaximumCurrentImax(A) Period1: 2504 |  |  |  | 1.674 | 11.334 | 200.7478 | 45.247
Eisenhüttenstadt (Abzweig) - Eisenhüttenstadt 548-2 | 11T0000000000023 | 50HERTZ | Eisenhüttenstadt (Abzweig) | Eisenhüttenstadt | 400 | MaximumCurrentImax(A) Period1: 1200 |  |  |  | 0.502 | 1.818 | 34.6204 | 7.526
Eisenhüttenstadt (Abzweig) - Preilack 548-1 | 11T0000000000023 | 50HERTZ | Eisenhüttenstadt (Abzweig) | Preilack | 400 | MaximumCurrentImax(A) Period1: 2280 |  |  |  | 1.422 | 9.63 | 170.8712 | 38.476
Heinersdorf - Heinersdorf (Abzweig) 548-3 | 11T0000000000023 | 50HERTZ | Heinersdorf | Heinersdorf (Abzweig) | 400 | MaximumCurrentImax(A) Period1: 2720 |  |  |  | 0.005 | 0.031 | 0.53407 | 0.123
Eisenhüttenstadt (Abzweig) - Heinersdorf (Abzweig) 548-4 | 11T0000000000023 | 50HERTZ | Eisenhüttenstadt (Abzweig) | Heinersdorf (Abzweig) | 400 | MaximumCurrentImax(A) Period1: 2504 |  |  |  | 1.674 | 11.334 | 200.7478 | 45.247
Bärwalde - Schmölln 551 | 11TD8L551------R | 50HERTZ | Bärwalde | Schmölln | 400 | MaximumCurrentImax(A) Period1: 3150 |  |  |  | 0.7441 | 11.506 | 218.969 | 45.911
Bärwalde - Schmölln 552 | 11TD8L552------J | 50HERTZ | Bärwalde | Schmölln | 400 | MaximumCurrentImax(A) Period1: 3150 |  |  |  | 0.7441 | 11.506 | 218.969 | 45.911
Hagenwerder - Schmölln 553 | 11TD8L553------B | 50HERTZ | Hagenwerder | Schmölln | 400 | MaximumCurrentImax(A) Period1: 2500 |  |  |  | 1.6516 | 14.496 | 252.3013 | 56.656
Hagenwerder - Schmölln 554 | 11TD8L554------3 | 50HERTZ | Hagenwerder | Schmölln | 400 | MaximumCurrentImax(A) Period1: 2500 |  |  |  | 1.6516 | 14.496 | 252.3013 | 56.656
Schmölln - Dresden/Süd 555 | 11TD8L555------W | 50HERTZ | Schmölln | Dresden/Süd | 400 | MaximumCurrentImax(A) Period1: 2500 |  |  |  | 1.0031 | 9.3866 | 163.0487 | 36.548
Schmölln - Dresden/Süd 556 | 11TD8L556------O | 50HERTZ | Schmölln | Dresden/Süd | 400 | MaximumCurrentImax(A) Period1: 2500 |  |  |  | 1.0031 | 9.3866 | 163.0487 | 36.548
Bärwalde - Streumen 557 | 11TD8L557------G | 50HERTZ | Bärwalde | Streumen | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 2.5843 | 24.182 | 404.3544 | 93.783
Bärwalde - Streumen 558 | 11TD8L558------8 | 50HERTZ | Bärwalde | Streumen | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 2.5843 | 24.182 | 404.3544 | 93.783
Preilack - Streumen 559 | 11TD8L559------0 | 50HERTZ | Preilack | Streumen | 400 | MaximumCurrentImax(A) Period1: 2040 |  |  |  | 3.0048 | 32.391 | 511.7969 | 121.222
Preilack - Streumen 560 | 11TD8L560------Q | 50HERTZ | Preilack | Streumen | 400 | MaximumCurrentImax(A) Period1: 2040 |  |  |  | 3.0048 | 32.391 | 537.904 | 121.222
Ragow - Streumen 561 | 11T0-0000-0043-3 | 50HERTZ | Ragow | Streumen | 400 | MaximumCurrentImax(A) Period1: 2040 |  |  |  | 2.9365 | 22.6101 | 385.0022 | 88.719
Ragow - Streumen 562 | 11TD8L562------A | 50HERTZ | Ragow | Streumen | 400 | MaximumCurrentImax(A) Period1: 2040 |  |  |  | 2.9365 | 22.6101 | 385.0022 | 88.719
Graustein - Bärwalde 565 | 11TD8L565------N | 50HERTZ | Graustein | Bärwalde | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 0.6666 | 5.5904 | 96.4155 | 21.801
Graustein - Bärwalde 566 | 11TD8L566------F | 50HERTZ | Graustein | Bärwalde | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 0.6666 | 5.5904 | 96.4155 | 21.801
Streumen - Röhrsdorf 571 | 11TD8L571------9 | 50HERTZ | Streumen | Röhrsdorf | 400 | MaximumCurrentImax(A) Period1: 2504 |  |  |  | 2.6478 | 19.844 | 385.7876 | 82.808
Streumen - Röhrsdorf 572 | 11TD8L572------1 | 50HERTZ | Streumen | Röhrsdorf | 400 | MaximumCurrentImax(A) Period1: 2504 |  |  |  | 2.6478 | 19.844 | 385.7876 | 82.808
Röhrsdorf - Weida 573 | 11TD8L573------U | 50HERTZ | Röhrsdorf | Weida | 400 | MaximumCurrentImax(A) Period1: 2504 |  |  |  | 2.5835 | 15.606 | 270.7425 | 61.654
Remptendorf - Röhrsdorf 574 | 11TD8L574------M | 50HERTZ | Remptendorf | Röhrsdorf | 400 | MaximumCurrentImax(A) Period1: 2504 |  |  |  | 4.2693 | 25.789 | 459.8349 | 103.396
Remptendorf - Weida 575 | 11TD8L575------E | 50HERTZ | Remptendorf | Weida | 400 | MaximumCurrentImax(A) Period1: 2504 |  |  |  | 1.8371 | 11.097 | 207.4079 | 45.505
Streumen - Eula 585 | 11TD8L585------5 | 50HERTZ | Streumen | Eula | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 2.9546 | 22.144 | 356.6964 | 84.359
Streumen - Eula 586 | 11TD8L586------Y | 50HERTZ | Streumen | Eula | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 2.9546 | 22.144 | 356.6964 | 84.359
Eula - Pulgar 587 | 11TD8L587------Q | 50HERTZ | Eula | Pulgar | 400 | MaximumCurrentImax(A) Period1: 2720 |  |  |  | 0.7639 | 4.9919 | 90.8549 | 20.185
Eula - Pulgar 588 | 11TD8L588------I | 50HERTZ | Eula | Pulgar | 400 | MaximumCurrentImax(A) Period1: 2720 |  |  |  | 0.7639 | 4.9919 | 90.8549 | 20.185
Pulgar - Vieselbach 589 | 11TD8L589------A | 50HERTZ | Pulgar | Vieselbach | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 3.2561 | 27.307 | 441.0796 | 104.4
Pulgar - Vieselbach 590 | 11TD8L590-----0Y | 50HERTZ | Pulgar | Vieselbach | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 3.2561 | 27.307 | 441.0796 | 104.4
Dresden/Süd - Röhrsdorf 591 | 11TD8L591------S | 50HERTZ | Dresden/Süd | Röhrsdorf | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 2.2251 | 22.06 | 380.6039 | 85.368
Dresden/Süd - Freiberg/Nord 592 | 11TD8L592------K | 50HERTZ | Dresden/Süd | Freiberg/Nord | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.1724 | 12.37 | 212.9686 | 47.765
Freiberg/Nord - Röhrsdorf 594 | 11TD8L594------4 | 50HERTZ | Freiberg/Nord | Röhrsdorf | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.0522 | 9.686 | 167.5726 | 37.587
Putlitz/Süd - Perleberg - Putlitz 596 | 11TD8L596------P | 50HERTZ | Putlitz/Süd | Perleberg - Putlitz | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 0.967 | 8.748 | 146.3354 | 34.208
Reuter - Mitte 903 | 11TD8L903------G | 50HERTZ | Reuter | Mitte | 400 | MaximumCurrentImax(A) Period1: 1620 |  |  |  | 0.267 | 2.372 | 769.6902 | 10.69
Reuter - Charlottenburg 904 | 11TD8L904------8 | 50HERTZ | Reuter | Charlottenburg | 400 | MaximumCurrentImax(A) Period1: 1620 |  |  |  | 0.1291 | 1.2745 | 235.6194 | 5.27
Charlottenburg - Mitte 906 | 11TD8L906------T | 50HERTZ | Charlottenburg | Mitte | 400 | MaximumCurrentImax(A) Period1: 1155 |  |  |  | 0.1206 | 1.2301 | 475.0716 | 5.42
Teufelsbruch - Reuter 907 | 11TD8L907------L | 50HERTZ | Teufelsbruch | Reuter | 400 | MaximumCurrentImax(A) Period1: 1620 |  |  |  | 0.151 | 1.6912 | 690.2079 | 7.55
Teufelsbruch - Reuter 908 | 11TD8L908------D | 50HERTZ | Teufelsbruch | Reuter | 400 | MaximumCurrentImax(A) Period1: 1620 |  |  |  | 0.151 | 1.6912 | 690.2079 | 7.55
Friedrichshain - Mitte 919 | 11TD8L919------X | 50HERTZ | Friedrichshain | Mitte | 400 | MaximumCurrentImax(A) Period1: 1660 |  |  |  | 0.131 | 1.513 | 368.3203 | 6.55
Friedrichshain - Mitte 920 | 11TD8L920------M | 50HERTZ | Friedrichshain | Mitte | 400 | MaximumCurrentImax(A) Period1: 1660 |  |  |  | 0.131 | 1.5196 | 376.5513 | 6.55
Friedrichshain - Marzahn 921 | 11TD8L921------E | 50HERTZ | Friedrichshain | Marzahn | 400 | MaximumCurrentImax(A) Period1: 1660 |  |  |  | 0.1076 | 1.2266 | 300.8389 | 5.38
Friedrichshain - Marzahn 922 | 11TD8L922------6 | 50HERTZ | Friedrichshain | Marzahn | 400 | MaximumCurrentImax(A) Period1: 1660 |  |  |  | 0.1124 | 1.2145 | 321.0079 | 5.35
Hamburg/Nord - Brunsbüttel 951 | 11TD8L951------O | 50HERTZ | Hamburg/Nord | Brunsbüttel | 400 | MaximumCurrentImax(A) Period1: 3600 |  |  |  | 1.07 | 13.95 | 283.9371 | 57.098
Hamburg/Nord - Brunsbüttel 952 | 11TD8L952------G | 50HERTZ | Hamburg/Nord | Brunsbüttel | 400 | MaximumCurrentImax(A) Period1: 3600 |  |  |  | 1.07 | 13.95 | 283.9371 | 57.098
Hamburg/Ost - Hamburg/Nord 961 | 11TD8L961------F | 50HERTZ | Hamburg/Ost | Hamburg/Nord | 400 | MaximumCurrentImax(A) Period1: 2580 |  |  |  | 1.0501 | 7.8803 | 139.204 | 31.001
Hamburg/Ost - Hamburg/Nord 962 | 11TD8L962------7 | 50HERTZ | Hamburg/Ost | Hamburg/Nord | 400 | MaximumCurrentImax(A) Period1: 2580 |  |  |  | 1.0501 | 7.8803 | 139.204 | 31.001
Hamburg/Süd - Hamburg/Ost 971 | 11TD8L971------6 | 50HERTZ | Hamburg/Süd | Hamburg/Ost | 400 | MaximumCurrentImax(A) Period1: 2580 |  |  |  | 0.9901 | 7.4404 | 131.9783 | 29.433
Krümmel - Hamburg/Süd 991-972 | 11T0-0000-0084-L | 50HERTZ | Krümmel | Hamburg/Süd | 400 | MaximumCurrentImax(A) Period1: 2580 |  |  |  | 1.5801 | 14.2168 | 273.6956 | 57.825
Hamburg/Ost - Krümmel 992 | 11TD8L992------H | 50HERTZ | Hamburg/Ost | Krümmel | 400 | MaximumCurrentImax(A) Period1: 3680 |  |  |  | 0.59 | 6.7764 | 141.7172 | 28.392
Y-Leupolz (-Bidingen - Oberottmarshausen) ALLG O | 11T0-0000-0698-C | Amprion GmbH | Leupolz | Y-Bidngen | 400 | [6 empty] | 2720 |  |  | 0.834 | 7.71 | 133.7 | 30.6594 | German internal tie-line
Y-Oberottmarshausen (-Bidingen - Leupolz) ALLG O | 11T0-0000-0769-G | Amprion GmbH | Oberottmarshausen | Y-Bidngen | 400 | [6 empty] | 2720 |  |  | 1.37 | 12.68 | 220.9 | 50.5393
Arpe - Uentrop ARPE W | 11T0-0000-0549-Y | Amprion GmbH | Arpe | Uentrop | 400 | [6 empty] | 2257 |  |  | 1.991 | 17.08 | 294.7 | 67.7494
Meitingen - Oberottmarshausen AUGSBU O | 11T0-0000-0724-A | Amprion GmbH | Meitingen | Oberottmarshausen | 400 | [6 empty] | 2720 |  |  | 1.408 | 13.26 | 221.6 | 51.764
Lechhausen - Oberottmarshausen AUGSBU W | 11T0-0000-0694-O | Amprion GmbH | Lechhausen | Oberottmarshausen | 400 | [6 empty] | 2720 |  |  | 0.961 | 9.01 | 152 | 35.3391
St. Barbara - Uchtelfangen BABARA | 11T0-0000-0506-M | Amprion GmbH | St Barbara | Uchtelfangen | 220 | [6 empty] | 1290 |  |  | 1.124 | 5.896 | 77.3 | 20.3864
Benteler - Hanekenfaehr BENTLR | 11T0-0000-0307-T | Amprion GmbH | Benteler | Hanekenfaehr | 220 | [6 empty] | 1282 |  |  | 0.073 | 0.373 | 4.6 | 1.2508
Meckenheim - Sechtem BGEIST W | 11T0-0000-0843-0 | Amprion GmbH | Meckenheim | Sechtem | 400 | [8 empty] | 2720 | 0.571 | 5.513 | 98.7 | 22.2753
Maximiliansau - Mutterstadt BIENWD W | 11T0-0000-0376-4 | Amprion GmbH | Maximiliansau | Mutterstadt | 220 | [8 empty] | 2000 | 2.585 | 13.81 | 182.5 | 47.9402
Y-Altenkleusheim (-Garenfeld - Opladen) BIGGE W | 11T0-0000-0114-7 | Amprion GmbH | Altenkleusheim | Y-Garenfeld | 220 | [8 empty] | 1282 | 4.915 | 21.15 | 144.2 | 52.7362
Y-Garenfeld (-Altenkleusheim - Opladen) BIGGE W | 11T0-0000-0274-F | Amprion GmbH | Garenfeld | Y-Garenfeld | 220 | [8 empty] | 1392 | 0.722 | 4.042 | 27.4 | 10.0495
Y-Opladen (-Altenkleusheim - Garenfeld) BIGGE W | 11T0-0000-0420-0 | Amprion GmbH | Opladen | Y-Garenfeld | 220 | [8 empty] | 1392 | 3.144 | 17.05 | 218 | 58.2186
Y-Altenkleusheim (-Bixterheide - Opladen) BIGGE O | 11T0-0000-0120-F | Amprion GmbH | Altenkleusheim | Y-Bixterheide | 220 | [8 empty] | 1282 | 4.915 | 21.16 | 144.3 | 52.767
Y-Bixterheide (-Altenkleusheim - Opladen) BIGGE O | 11T0-0000-0175-H | Amprion GmbH | Bixterheide | Y-Bixterheide | 220 | [8 empty] | 1392 | 0.665 | 3.721 | 43.6 | 12.1631
Y-Opladen (-Altenkleusheim - Bixterheide) BIGGE O | 11T0-0000-0419-E | Amprion GmbH | Opladen | Y-Bixterheide | 220 | [8 empty] | 1392 | 3.144 | 17.05 | 218.1 | 58.232
Bixterheide - Garenfeld BIXTRH N | 11T0-0000-0272-L | Amprion GmbH | Bixterheide | Garenfeld | 220 | [8 empty] | 1392 | 1.377 | 7.707 | 70.6 | 22.2749
Mittelbexbach - Uchtelfangen BLIES N | 11T0-0000-0740-E | Amprion GmbH | Mittelbexbach | Uchtelfangen | 400 | [8 empty] | 3150 | 0.598 | 5.092 | 88.8 | 20.3059
Mittelbexbach - Uchtelfangen BLIES S | 11T0-0000-0741-B | Amprion GmbH | Mittelbexbach | Uchtelfangen | 400 | [8 empty] | 3150 | 0.598 | 5.107 | 88.6 | 20.3129
Y-Y (-Buers - Hoheneck - Tiengen - Werben) BLUDNZ W | 11T0-0000-1620-L | Amprion GmbH | Y-Werben | Y-Herbertingen | 220 | [6 empty] | 896 |  |  | 3.532 | 33.4 | 253.9 | 87.9379
Y-Buers (-Hoheneck - Tiengen - Werben) BLUDNZ W | 11T-D4-D7-00001W | Amprion GmbH | Y-Werben | Bürs | 220 | [6 empty] | 1710 |  |  | 0.592 | 9.08 | 70.4 | 24.1435
Y-Hoheneck (-Buers - Tiengen - Werben) BLUDNZ W | 11T0-0000-0961-U | Amprion GmbH | Hoheneck | Y-Herbertingen | 220 | [6 empty] | 1026 |  |  | 4.648 | 41.93 | 412.2 | 125.5416
Y-Tiengen (-Buers - Hoheneck - Werben) BLUDNZ W | 11T0-0000-0962-R | Amprion GmbH | Tiengen | Y-Herbertingen | 220 | [6 empty] | 896 |  |  | 7.506 | 47.6 | 299.7 | 114.056
Bochum - Eiberg BOCHUM W | 11T0-0000-0176-E | Amprion GmbH | Bochum | Eiberg | 220 | [8 empty] | 2000 | 0.735 | 3.877 | 47 | 12.8905
Bocklemuend - Brauweiler BOCKLE N | 11T0-0000-0194-C | Amprion GmbH | Bocklemuend | Brauweiler | 220 | [6 empty] | 718 |  |  | 0.273 | 1.419 | 17.2 | 4.7177
Bocklemuend - Brauweiler BOCKLE S | 11T0-0000-0195-9 | Amprion GmbH | Bocklemuend | Brauweiler | 220 | [6 empty] | 718 |  |  | 0.273 | 1.419 | 17.2 | 4.7177
Luestringen - Wehrendorf BOHMTE W | 11T0-0000-0535-D | Amprion GmbH | Luestringen | Wehrendorf | 220 | [6 empty] | 740 |  |  | 1.611 | 7.566 | 64.8 | 21.1442
Hanekenfaehr - Westerkappeln BRAMGAU | 11T0-0000-0642-D | Amprion GmbH | Hanekenfaehr | Westerkappeln | 400 | [6 empty] | 2565 |  |  | 1.65 | 15.26 | 264.5 | 60.6683
Brauweiler - Rommerskirchen BRAUWL W | 11T0-0000-0927-S | Amprion GmbH | Brauweiler | Rommerskirchen 1 | 400 | [8 empty] | 3150 | 0.122 | 2.485 | 41.7 | 9.7208
Bergmannsglueck - Buescherhof BUER S | 11T0-0000-0164-O | Amprion GmbH | Bergmannsglueck | Buescherhof | 220 | [6 empty] | 1290 |  |  | 0.829 | 4.941 | 67.3 | 17.4135
Buerstadt - Lambsheim BUERST W | 11T0-0000-0568-T | Amprion GmbH | Buerstadt | Lambsheim | 400 | [8 empty] | 3150 | 0.455 | 4.226 | 73.6 | 16.8413
Y-Buescherhof (-Karnap - Rosenblumendelle) BUESHR W | 11T0-0000-0576-V | Amprion GmbH | Buescherhof | Y-Karnap | 400 | [6 empty] | 2720 |  |  | 0.146 | 1.341 | 23.4 | 5.3493
Y-Karnap (-Buescherhof - Rosenblumendelle) BUESHR W | 11T0-0000-0657-V | Amprion GmbH | Karnap | Y-Karnap | 400 | [6 empty] | 2720 |  |  | 0.024 | 0.235 | 3.7 | 0.89044
Y-Rosenblumendelle (-Buescherhof - Karnap) BUESHR W | 11T0-0000-0838-Q | Amprion GmbH | Rosenblumendelle | Y-Karnap | 400 | [6 empty] | 2720 |  |  | 0.303 | 2.847 | 47.8 | 11.1398
Brauweiler - Knapsack BURBAC O | 11T0-0000-0928-P | Amprion GmbH | Brauweiler | Knapsack | 400 | [8 empty] | 3150 | 0.345 | 3.197 | 55.1 | 12.6741
Y-Gersteinwerk (-Poeppingshausen - Ruhrzink) CAPPEN N | 11T0-0000-0280-N | Amprion GmbH | Gersteinwerk | Y-Poeppinghausen | 220 | [8 empty] | 1539 | 1.655 | 8.937 | 110.2 | 29.968
Y-Poeppinghausen (-Gersteinwerk - Ruhrzink) CAPPEN N | 11T0-0000-0441-Q | Amprion GmbH | Poeppinghausen | Y-Poeppinghausen | 220 | [8 empty] | 1539 | 0.558 | 3.074 | 21.5 | 7.7632
Y-Ruhrzink (-Gersteinwerk - Poeppinghausen) CAPPEN N | 11T0-0000-0464-9 | Amprion GmbH | Ruhrzink | Y-Poeppinghausen | 220 | [8 empty] | 1539 | 0.088 | 0.695 | 4.8 | 1.7442
Elmenhorst - Gersteinwerk CAPPEN S | 11T0-0000-0282-H | Amprion GmbH | Elmenhorst | Gersteinwerk | 220 | [8 empty] | 1392 | 1.509 | 8.233 | 102.2 | 27.6998
Datteln - Mengede DATTLN O | 11T0-0000-0727-1 | Amprion GmbH | Datteln | Mengede | 400 | [6 empty] | 2720 |  |  | 0.271 | 2.562 | 42.6 | 9.9762
Datteln - Mengede DATTLN W | 11T0-0000-0728-Z | Amprion GmbH | Datteln | Mengede | 400 | [6 empty] | 2720 |  |  | 0.271 | 2.566 | 42.6 | 9.984
Dauersberg - Linde DAURSB O | 11T0-0000-0706-C | Amprion GmbH | Dauersberg | Linde | 400 | [6 empty] | 2720 |  |  | 2.009 | 18.56 | 322.3 | 73.8568
Dauersberg - Halfeshof DAURSB W | 11T0-0000-0632-H | Amprion GmbH | Dauersberg | Halfeshof | 400 | [6 empty] | 2720 |  |  | 2.294 | 21.19 | 368.4 | 84.3717
Y-Buers (-Voehringen - Werben) DELLM O | 11T0-0000-0954-P | Amprion GmbH | Y-Werben | Bürs | 220 | [6 empty] | 1710 |  |  | 0.513 | 9.13 | 69.7 | 24.0892
Y-Voehringen (-Buers - Werben) DELLM O | 11T0-0000-1374-4 | Amprion GmbH | Voehringen | Y-Werben | 220 | [6 empty] | 1220 |  |  | 6.622 | 42.77 | 431.6 | 129.7423
Hamborn - Niederrhein DINSLK W | 11T0-0000-0382-C | Amprion GmbH | Hamborn | Niederrhein | 220 | [7 empty] | 841 | 1031 | 0.682 | 5.168 | 77.8 | 19.148
Y-Hoheneck (-Dellmensingen - Voehringen) DONAU O | 11T0-0000-0957-G | Amprion GmbH | Hoheneck | Y-Voehringen | 400 | [6 empty] | 2440 |  |  | 2.849 | 25.57 | 418.5 | 98.7835
Y-Voehringen (-Dellmensingen - Hoheneck) DONAU O | 11T0-0000-0956-J | Amprion GmbH | Voehringen | Y-Voehringen | 400 | [6 empty] | 2720 |  |  | 0.465 | 4.311 | 74.7 | 17.1364
Y-Dellmensingen (-Hoheneck - Voehringen) DONAU O | 11T-D4-D7-00023M | Amprion GmbH | Y-Voehringen | Dellmensingen | 400 | [6 empty] | 2720 |  |  | 0.004 | 0.05 | 0.7 | 0.17865
Dellmensingen - Voehringen DONAU W | 11T-D4-D7-00005O | Amprion GmbH | Voehringen | Dellmensingen | 400 | [6 empty] | 2580 |  |  | 0.247 | 2.107 | 36.7 | 8.3972
Y-St. Huelfe (-Ohlensehlen - Wehrendorf) DUEMM S1 | 11T0-0000-0996-3 | Amprion GmbH | St Huelfe | Y-St Huelfe | 400 | [6 empty] | 481 |  |  | 0.157 | 2.984 | 90 | 15.6492
Y-Wehrendorf (-Ohlensehlen - St. Huelfe) DUEMM S1 | 11T0-0000-0978-5 | Amprion GmbH | Wehrendorf | Y-St Huelfe | 400 | [6 empty] | 2720 |  |  | 0.509 | 5.485 | 90 | 21.2169
Y-Ohlensehlen (-St. Huelfe - Wehrendorf) DUEMM S1 | 11T0-0000-1115-Z | Amprion GmbH | Y-St Huelfe | Ohlensehlen | 400 | [6 empty] | 2616 |  |  | 0.62 | 5.24 | 88.8 | 20.5989
Duennwald - Opladen DUENNW O | 11T0-0000-0413-W | Amprion GmbH | Duennwald | Opladen | 220 | [8 empty] | 1548 | 0.593 | 3.479 | 31.4 | 9.9808
Duennwald - Opladen DUENNW W | 11T0-0000-1376-Z | Amprion GmbH | Duennwald | Opladen | 220 | [8 empty] | 1548 | 0.591 | 3.479 | 31.5 | 9.9966
Eiberg - Karnap EIBERG N | 11T0-0000-0654-3 | Amprion GmbH | Eiberg | Karnap | 400 | [6 empty] | 2580 |  |  | 0.394 | 3.635 | 63 | 14.4509
Y-Altenkleusheim (-Eiserfeld - Setzer Wiese) EISERF | 11T0-0000-0121-C | Amprion GmbH | Altenkleusheim | Y-Setzer Wiese | 220 | [6 empty] | 740 |  |  | 0.686 | 2.938 | 20.1 | 7.3383
Y-Eiserfeld (-Altenkleusheim - Setzerwiese) EISERF | 11T0-0000-0248-F | Amprion GmbH | Eiserfeld | Y-Setzer Wiese | 220 | [6 empty] | 960 |  |  | 1.148 | 5.413 | 59.2 | 17.0943
Y-Setzer Wiese (-Altenkleusheim - Eiserfeld) EISERF | 11T0-0000-1377-W | Amprion GmbH | Setzer Wiese | Y-Setzer Wiese | 220 | [6 empty] | 1360 |  |  | 0.315 | 1.688 | 22.1 | 5.8325
Diefflen - Uchtelfangen ELLBCH N | 11T0-0000-1673-T | Amprion GmbH | Diefflen | Uchtelfangen | 220 | [6 empty] | 1360 |  |  | 1.1 | 6.27 | 85.9 | 22.1616
Eller - Opladen ELLER O | 11T0-0000-0253-Q | Amprion GmbH | Eller | Opladen | 220 | [8 empty] | 1539 | 1.269 | 6.745 | 108.7 | 25.8569
Eller - St. Peter ELLER W | 11T0-0000-0495-V | Amprion GmbH | Eller | St Peter | 220 | [7 empty] | 1104 | 1344 | 0.919 | 5.496 | 51.4 | 16.05
Y-Elmenhorst (-Poeppinghausen - Ruhrzink) ELMENH S | 11T0-0000-0259-8 | Amprion GmbH | Elmenhorst | Y-Elmenhorst | 220 | [6 empty] | 1539 |  |  | 0.542 | 3.039 | 39 | 10.3961
Y-Poeppinghausen (-Elmenhorst - Ruhrzink) ELMENH S | 11T0-0000-0442-N | Amprion GmbH | Poeppinghausen | Y-Elmenhorst | 220 | [6 empty] | 1539 |  |  | 0.554 | 3.056 | 21.3 | 7.7044
Y-Ruhrzink (-Elmenhorst - Poeppinghausen) ELMENH S | 11T0-0000-0465-6 | Amprion GmbH | Ruhrzink | Y-Elmenhorst | 220 | [6 empty] | 1539 |  |  | 0.088 | 0.695 | 4.8 | 1.7442
Buescherhof - Hamborn EMSHER N | 11T0-0000-0207-Y | Amprion GmbH | Buescherhof | Hamborn | 220 | [6 empty] | 1160 |  |  | 0.604 | 3.129 | 37.9 | 10.3991
Buescherhof - Hamborn EMSHER S | 11T0-0000-0208-V | Amprion GmbH | Buescherhof | Hamborn | 220 | [6 empty] | 1160 |  |  | 0.603 | 3.124 | 37.9 | 10.3907 | German internal tie-line
Meppen - Niederlangen EMSLD OW | 11T0-0000-0983-G | Amprion GmbH | Meppen | Y-Niederlangen | 400 | [6 empty] | 3150 |  |  | 0.257 | 2.883 | 37.4 | 9.9158
Doerpen West - Hanekenfaehr EMSLD WB | 11T-D2-D7-00002F | Amprion GmbH | Hanekenfaehr | Doerpen West | 400 | [6 empty] | 3150 |  |  | 1.115 | 10.78 | 164.8 | 40.2494
Diefflen - Ensdorf ENSDF N | 11T0-0000-1672-W | Amprion GmbH | Diefflen | Ensdorf | 220 | [6 empty] | 1160 |  |  | 0.66 | 3.7 | 56.9 | 13.8557
Y-Ensdorf (-Diefflen - Uchtelfangen) ENSDF S | 11T0-0000-0265-G | Amprion GmbH | Ensdorf | Y-Diefflen | 220 | [7 empty] | 740 | 1031 | 0.34 | 1.9 | 40 | 8.3249
Y-Diefflen (-Ensdorf - Uchtelfangen) ENSDF S | 11T0-0000-0218-R | Amprion GmbH | Diefflen | Y-Diefflen | 220 | [6 empty] | 1360 |  |  | 0.2 | 1.34 | 19.9 | 4.9312
Y-Uchtelfangen (-Diefflen - Ensdorf) ENSDF S | 11T0-0000-0511-X | Amprion GmbH | Uchtelfangen | Y-Diefflen | 220 | [6 empty] | 1360 |  |  | 0.94 | 5.15 | 108.7 | 22.5938 | German internal tie-line
Bauler - Niederstedem ENZ N | 11T0-0000-0149-H | Amprion GmbH | Bauler | Niederstedem | 220 | [8 empty] | 1920 | 0.599 | 5.75 | 80.4 | 20.5321
Bauler - Niederstedem ENZ S | 11T0-0000-0150-3 | Amprion GmbH | Bauler | Niederstedem | 220 | [8 empty] | 1920 | 0.599 | 5.758 | 80.6 | 20.5719
Urberach (NEU) - Urberach ERLENSEE | 11T0-0000-1382-6 | Amprion GmbH | Urberach (NEU) | Urberach | 400 | [6 empty] | 3150 |  |  | 0.005 | 0.053 | 0.8 | 0.19663
Bischofsheim - Urberach ERZHAU N | 11T0-0000-0560-G | Amprion GmbH | Bischofsheim | Urberach | 400 | [8 empty] | 2720 | 1.271 | 12.33 | 198.4 | 47.2306
Buescherhof - Nordlicht ESSEN W | 11T0-0000-0763-Y | Amprion GmbH | Buescherhof | Nordlicht | 400 | [6 empty] | 2720 |  |  | 0.397 | 3.681 | 63.6 | 14.6111
Duelken - Osterath FICHTH O | 11T0-0000-0230-6 | Amprion GmbH | Duelken | Osterath | 220 | [6 empty] | 1282 |  |  | 1.274 | 9.071 | 143.5 | 34.4528
Edelstahl - Osterath FICHTH W | 11T0-0000-0237-M | Amprion GmbH | Edelstahl | Osterath | 220 | [8 empty] | 1290 | 0.481 | 2.493 | 32.8 | 8.6351
Bayer - Duennwald FLITTA O | 11T0-0000-0233-Y | Amprion GmbH | Bayer | Duennwald | 220 | [6 empty] | 623 |  |  | 0.141 | 0.676 | 219.9 | 11.6428
Y-Gohrpunkt (-Osterath - Rommerskirchen) FRIXHM N | 11T0-0000-1390-8 | Amprion GmbH | Gohrpunkt | Y-Osterath | 220 | [6 empty] | 820 |  |  | 0.005 | 0.05 | 0.4 | 0.13505
Y-Osterath (-Gohrpunkt - Rommerskirchen) FRIXHM N | 11T0-0000-1388-P | Amprion GmbH | Osterath | Y-Osterath | 220 | [8 empty] | 1360 | 1.077 | 5.817 | 76.1 | 20.0915
Y-Rommerskirchen (-Gohrpunkt - Osterath) FRIXHM N | 11T0-0000-1389-M | Amprion GmbH | Rommerskirchen | Y-Osterath | 220 | [8 empty] | 1360 | 0.582 | 3.131 | 40.7 | 10.7798
Rommerskirchen - St Peter FRIXHM S | 11T0-0000-1862-Q | Amprion GmbH | St Peter | Rommerskirchen | 220 | [6 empty] | 1290 |  |  | 1.048 | 5.61 | 77.7 | 19.9372
Y-Geithe (-Lippborg - Uentrop) GEITHE W | 11T0-0000-0608-B | Amprion GmbH | Geithe | Y-Lippborg | 400 | [8 empty] | 2720 | 0.091 | 0.935 | 19.5 | 4.0775
Y-Lippborg (-Geithe - Uentrop) GEITHE W | 11T0-0000-0711-N | Amprion GmbH | Lippborg | Y-Lippborg | 400 | [8 empty] | 673 | 0.006 | 0.055 | 1 | 0.22395
Y-Uentrop (-Geithe - Lippborg) GEITHE W | 11T0-0000-0866-K | Amprion GmbH | Uentrop | Y-Lippborg | 400 | [8 empty] | 2580 | 0.031 | 0.28 | 4.3 | 1.0478
Gellep - Osterath GELLEP W | 11T0-0000-0275-C | Amprion GmbH | Gellep | Osterath | 220 | [6 empty] | 1255 |  |  | 0.554 | 3.129 | 29.7 | 9.2056
Daxlanden - Weingarten GERMHM S | 11T-D4-D7-00003S | Amprion GmbH | Weingarten | Daxlanden | 400 | [6 empty] | 2720 |  |  | 0.444 | 4.088 | 71.4 | 16.3146
Y-Gersteinwerk (-Guetersloh - Uentrop) GERSTE O | 11T0-0000-0941-1 | Amprion GmbH | Gersteinwerk | Y-Gersteinwerk | 400 | [8 empty] | 3096 | 0.363 | 3.133 | 54.2 | 12.4437
Y-Guetersloh (-Gersteinwerk - Uentrop) GERSTE O | 11T0-0000-0943-W | Amprion GmbH | Guetersloh | Y-Gersteinwerk | 400 | [8 empty] | 3096 | 1.181 | 10.62 | 198.8 | 43.8775
Y-Uentrop (-Gersteinwerk - Guetersloh) GERSTE O | 11T0-0000-0942-Z | Amprion GmbH | Uentrop | Y-Gersteinwerk | 400 | [8 empty] | 2720 | 0.405 | 3.767 | 64.6 | 14.8965
Niederstedem - Osburg GILZEM O | 11T0-0000-0755-W | Amprion GmbH | Niederstedem | Osburg | 400 | [6 empty] | 2580 |  |  | 1.356 | 11.62 | 201.5 | 46.2074
Y-Bergmannsglueck (-Eiberg - Gelsenberg) GLADBK W | 11T0-0000-0169-9 | Amprion GmbH | Bergmannsglueck | Y-Gelsenberg | 220 | [8 empty] | 1290 | 0.434 | 2.56 | 27.1 | 7.9538
Y-Eiberg (-Bergmannsglueck - Gelsenberg) GLADBK W | 11T0-0000-0246-L | Amprion GmbH | Eiberg | Y-Gelsenberg | 220 | [8 empty] | 1290 | 0.924 | 5.15 | 46.1 | 14.7138
Y-Gelsenberg (-Bergmannsglueck - Eiberg) GLADBK W | 11T0-0000-0279-0 | Amprion GmbH | Gelsenberg | Y-Gelsenberg | 220 | [8 empty] | 1290 | 0.005 | 0.05 | 0.4 | 0.13505
Y-Bollenacker (-Brauweiler - Sechtem) GODORF O | 11T0-0000-1392-2 | Amprion GmbH | Bollenacker | Y-Bollenacker | 220 | [6 empty] | 1290 |  |  | 0.16 | 0.86 | 10 | 2.8004
Y-Brauweiler (-Bollenacker - Sechtem) GODORF O | 11T0-0000-1394-X | Amprion GmbH | Brauweiler | Y-Bollenacker | 220 | [6 empty] | 1300 |  |  | 0.863 | 5.5 | 92.8 | 21.5738
Y-Sechtem (-Brauweiler - Bollenacker) GODORF O | 11T0-0000-1395-U | Amprion GmbH | Sechtem | Y-Bollenacker | 220 | [6 empty] | 1290 |  |  | 0.1 | 1.72 | 29.8 | 6.8367
Daxlanden - Maximiliansau GOLDGR | 11T-D4-D7-00002U | Amprion GmbH | Maximiliansau | Daxlanden | 220 | [6 empty] | 2500 |  |  | 0.079 | 0.729 | 12.2 | 2.8478
Y-Hanekenfaehr (-Gronau - Kusenhorst) GRAFSH W | 11T0-0000-0311-6 | Amprion GmbH | Hanekenfaehr | Y-Hanekenfaehr | 220 | [8 empty] | 1300 | 2.45 | 20.06 | 175.6 | 56.676
Y-Kusenhorst (-Gronau - Hanekenfaehr) GRAFSH W | 11T0-0000-0344-M | Amprion GmbH | Kusenhorst | Y-Hanekenfaehr | 220 | [8 empty] | 1300 | 3.294 | 27.52 | 172.3 | 65.7564
Y-Gremberghoven (-Siegburg - Stockem) GREMBG O | 11T0-0000-1397-O | Amprion GmbH | Gremberghoven | Y-Stockem | 220 | [6 empty] | 700 |  |  | 0.714 | 3.762 | 43.7 | 12.2439
Y-Siegburg (-Gremberghoven - Stockem) GREMBG O | 11T0-0000-1398-L | Amprion GmbH | Siegburg | Y-Stockem | 220 | [6 empty] | 1290 |  |  | 0.469 | 2.523 | 31.3 | 8.486
Y-Stockem (-Gremberghoven - Siegburg) GREMBG O | 11T0-0000-1399-I | Amprion GmbH | Stockem | Y-Stockem | 220 | [6 empty] | 700 |  |  | 0.005 | 0.05 | 0.4 | 0.13505
Gremberghoven - Siegburg GREMBG W | 11T0-0000-1402-X | Amprion GmbH | Gremberghoven | Siegburg | 220 | [6 empty] | 1290 |  |  | 1.19 | 6.288 | 74.2 | 20.6267
Pfungstadt - Urberach (NEU) GRIESH O | 11T0-0000-0872-S | Amprion GmbH | Pfungstadt | Urberach (NEU) | 400 | [8 empty] | 3150 | 0.934 | 8.773 | 150.6 | 34.7103
Reisholz - St Peter GRIND S | 11T0-0000-1863-N | Amprion GmbH | St Peter | Reisholz | 220 | [6 empty] | 1290 |  |  | 0.32 | 1.75 | 20.7 | 5.7475
Gronau - Hanekenfaehr GRONAU W | 11T0-0000-0617-A | Amprion GmbH | Gronau | Hanekenfaehr | 400 | [8 empty] | 3150 | 1.372 | 12.57 | 189.5 | 46.6062
Gundelfingen - Voehringen GUENZ N | 11T0-0000-0625-C | Amprion GmbH | Gundelfingen | Voehringen | 400 | [6 empty] | 2720 |  |  | 1.225 | 11.65 | 201.8 | 46.3015
Gundelfingen - Voehringen GUENZ S | 11T0-0000-0626-9 | Amprion GmbH | Gundelfingen | Voehringen | 400 | [6 empty] | 2720 |  |  | 1.255 | 11.61 | 201.5 | 46.1876
Y-Enniger (-Guetersloh - Uentrop) GUETER S | 11T0-0000-0603-Q | Amprion GmbH | Enniger | Y-Guetersloh | 400 | [6 empty] | 718 |  |  | 0.005 | 0.05 | 0.4 | 0.13505
Y-Guetersloh (-Enniger - Uentrop) GUETER S | 11T0-0000-0631-K | Amprion GmbH | Guetersloh | Y-Guetersloh | 400 | [6 empty] | 2565 |  |  | 0.792 | 7.143 | 134.1 | 29.5547
Y-Uentrop (-Enniger - Guetersloh) GUETER S | 11T0-0000-0867-H | Amprion GmbH | Uentrop | Y-Guetersloh | 400 | [6 empty] | 2565 |  |  | 0.797 | 6.966 | 124.8 | 28.156
Y-Kruckel (-Lippborg - Uentrop) HAARST O | 11T0-0000-0677-N | Amprion GmbH | Kruckel | Y-Lippborg | 400 | [6 empty] | 3150 |  |  | 0.666 | 12.98 | 240.1 | 53.3095
Y-Lippborg (-Kruckel - Uentrop) HAARST O | 11T0-0000-0712-K | Amprion GmbH | Lippborg | Y-Lippborg | 400 | [6 empty] | 3150 |  |  | 0.007 | 0.07 | 1.2 | 0.27676
Y-Uentrop (-Kruckel - Lippborg) HAARST O | 11T0-0000-0868-E | Amprion GmbH | Uentrop | Y-Lippborg | 400 | [6 empty] | 3150 |  |  | 0.029 | 0.261 | 4.1 | 0.98783
Geithe - Unna HAARST W | 11T0-0000-0607-E | Amprion GmbH | Geithe | Unna | 400 | [6 empty] | 2720 |  |  | 0.429 | 7.41 | 136 | 30.3145
Gronau - Kusenhorst HAMALD | 11T0-0000-0618-7 | Amprion GmbH | Gronau | Kusenhorst | 400 | [8 empty] | 3150 | 1.89 | 17.33 | 259.9 | 64.0876
St. Barbara - Mittelbexbach HAGARD O | 11T0-0000-0738-V | Amprion GmbH | St Barbara | Mittelbexbach | 400 | [6 empty] | 673 |  |  | 0.035 | 0.364 | 5.4 | 1.3388
St. Barbara - Mittelbexbach HAGARD W | 11T0-0000-0739-S | Amprion GmbH | St Barbara | Mittelbexbach | 400 | [6 empty] | 673 |  |  | 0.036 | 0.375 | 5.6 | 1.3838
Dauersberg - Setzer Wiese HELLER O | 11T0-0000-1409-C | Amprion GmbH | Dauersberg | Setzer Wiese | 220 | [6 empty] | 1360 |  |  | 2.565 | 13.88 | 178.3 | 47.5053
Dauersberg - Setzer Wiese HELLER W | 11T0-0000-0480-D | Amprion GmbH | Dauersberg | Setzer Wiese | 220 | [6 empty] | 1310 |  |  | 2.347 | 13.64 | 193.8 | 49.0971
Hoheneck - Herbertingen HERBTG W | 11T0-0000-0963-O | Amprion GmbH | Hoheneck | Herbertingen | 400 | [6 empty] | 2552 |  |  | 0.748 | 7.86 | 137.4 | 31.3817
Eiberg - Garenfeld HERDEK N | 11T0-0000-0243-U | Amprion GmbH | Eiberg | Garenfeld | 220 | [7 empty] | 1217 | 1310 | 2.742 | 15.17 | 154.1 | 46.1706
Eiberg - Garenfeld HERDEK S | 11T0-0000-0244-R | Amprion GmbH | Eiberg | Garenfeld | 220 | [7 empty] | 1140 | 1310 | 2.582 | 14.82 | 107.4 | 38.0976
Kriftel - Limburg HESSEN O | 11T0-0000-0702-O | Amprion GmbH | Kriftel | Limburg | 400 | [6 empty] | 2720 |  |  | 1.558 | 14.9 | 241.6 | 57.2945
Kusenhorst - Poeppinghausen HOCHLR O | 11T0-0000-0340-Y | Amprion GmbH | Kusenhorst | Poeppinghausen | 220 | [6 empty] | 1290 |  |  | 1.303 | 8.266 | 104.8 | 28.106
Y-Bochum (-Kusenhorst - Poeppinghausen) HOCHLR W | 11T0-0000-0183-J | Amprion GmbH | Bochum | Y-Poeppinghausen | 220 | [6 empty] | 1282 |  |  | 0.688 | 3.755 | 40.3 | 11.7471
Y-Kusenhorst (-Bochum - Poeppinghausen) HOCHLR W | 11T0-0000-0345-J | Amprion GmbH | Kusenhorst | Y-Poeppinghausen | 220 | [6 empty] | 1282 |  |  | 0.68 | 5.104 | 65.7 | 17.4868
Y-Poeppinghausen (-Bochum - Kusenhorst) HOCHLR W | 11T0-0000-0443-K | Amprion GmbH | Poeppinghausen | Y-Poeppinghausen | 220 | [6 empty] | 1282 |  |  | 0.619 | 3.125 | 38.9 | 10.5286 | German internal tie-line
Eiberg - Huellen HUELLN W | 11T0-0000-0651-C | Amprion GmbH | Eiberg | Huellen | 400 | [8 empty] | 3150 | 0.334 | 2.88 | 49.9 | 11.4477
Ibbenbueren - Westerkappeln IBBENB S | 11T0-0000-0911-D | Amprion GmbH | Ibbenbueren | Westerkappeln | 400 | [6 empty] | 615 |  |  | 0.343 | 3.153 | 55.4 | 12.6208
Y-Lambsheim (-Mittelbexbach - Otterbach) KAILAU N | 11T0-0000-0693-R | Amprion GmbH | Lambsheim | Y-Otterbach | 400 | [8 empty] | 3096 | 1.35 | 12.46 | 217.2 | 49.6776
Y-Mittelbexbach (-Lambsheim - Otterbach) KAILAU N | 11T0-0000-0742-8 | Amprion GmbH | Mittelbexbach | Y-Otterbach | 400 | [8 empty] | 3096 | 1.18 | 10.06 | 174.7 | 40.0329
Y-Otterbach (-Lambsheim - Mittelbexbach) KAILAU N | 11T0-0000-0809-Z | Amprion GmbH | Otterbach | Y-Otterbach | 400 | [8 empty] | 3096 | 0.015 | 0.138 | 2.5 | 0.56089
Lambsheim - Otterbach KAILAU S | 11T0-0000-0688-G | Amprion GmbH | Lambsheim | Otterbach | 400 | [8 empty] | 3096 | 1.474 | 12.59 | 219.1 | 50.154
Dettingen - Urberach KARLST S | 11T0-0000-0871-V | Amprion GmbH | Dettingen | Urberach | 400 | [8 empty] | 3150 | 0.56 | 5.2 | 90.4 | 20.7041
Fuehlingen - Opladen KASSEL S | 11T0-0000-0414-T | Amprion GmbH | Fuehlingen | Opladen | 220 | [6 empty] | 1360 |  |  | 0.257 | 1.387 | 17.9 | 4.7581
Bischofsheim - Kelsterbach KELSTB N | 11T0-0000-0658-S | Amprion GmbH | Bischofsheim | Kelsterbach | 400 | [6 empty] | 2500 |  |  | 0.501 | 4.955 | 91.3 | 20.3109
Hattingen - Witten KEMNAD S | 11T0-0000-0915-1 | Amprion GmbH | Hattingen | Witten | 400 | [8 empty] | 3096 | 0.495 | 4.37 | 76.6 | 17.4714
Leupolz - Woringen KEMPTE O | 11T0-0000-0918-T | Amprion GmbH | Leupolz | Woringen | 400 | [6 empty] | 2760 |  |  | 0.695 | 6.702 | 116.2 | 26.6487
Oberzier - Siersdorf KIRCHB S | 11T0-0000-0776-L | Amprion GmbH | Oberzier | Siersdorf | 400 | [8 empty] | 3150 | 0.658 | 6.087 | 105.6 | 24.2106
Kruckel - Mengede KIRCHL O | 11T0-0000-0730-I | Amprion GmbH | Kruckel | Mengede | 400 | [8 empty] | 2720 | 0.45 | 4.181 | 72.1 | 16.5798
Osterath - Rommerskirchen KNESTE W | 11T0-0000-0802-J | Amprion GmbH | Osterath | Rommerskirchen | 400 | [6 empty] | 2720 |  |  | 0.828 | 7.666 | 133.9 | 30.5947
Koblenz - Weissenthurm KOBLNZ N | 11T0-0000-0897-5 | Amprion GmbH | Koblenz | Weissenthurm | 400 | [6 empty] | 2580 |  |  | 0.311 | 2.714 | 47.5 | 10.8423
Wengerrohr - Weissenthurm KONDLW | 11T0-0000-0540-O | Amprion GmbH | Wengerrohr | Weissenthurm | 220 | [8 empty] | 1539 | 3.45 | 21.77 | 286.3 | 75.3896
Kuehmoos - Tiengen KUEMOS | 11T-D4-D7-00012R | Amprion GmbH | Tiengen | Kuehmoos | 220 | [6 empty] | 1290 |  |  | 0.672 | 3.532 | 81.4 | 16.1918
Hoheneck - Rheinau KUGELB O | 11T0-0000-0566-Z | Amprion GmbH | Hoheneck | Rheinau | 400 | [8 empty] | 3096 | 2.494 | 21.35 | 369.8 | 84.8504 | German internal tie-line
Hoheneck - Rheinau KUGELB W | 11T0-0000-0567-W | Amprion GmbH | Hoheneck | Rheinau | 400 | [8 empty] | 3096 | 2.474 | 21.32 | 369.4 | 84.7449
Buerstadt - Rheinau KURPFA O | 11T0-0000-1421-S | Amprion GmbH | Buerstadt | Rheinau | 400 | [8 empty] | 3096 | 0.795 | 6.793 | 117.8 | 27.0131 | German internal tie-line
Buerstadt - Rheinau KURPFA W | 11T0-0000-1422-P | Amprion GmbH | Buerstadt | Rheinau | 400 | [8 empty] | 3096 | 0.794 | 6.792 | 117.7 | 26.9997
Kusenhorst - Rosenblumendelle KUSENH | 11T0-0000-0681-0 | Amprion GmbH | Kusenhorst | Rosenblumendelle | 400 | [6 empty] | 2580 |  |  | 1.13 | 10.6 | 173.7 | 40.9755
Hattingen - Laer LAER W | 11T0-0000-0314-Y | Amprion GmbH | Hattingen | Laer | 220 | [6 empty] | 1290 |  |  | 0.916 | 5.588 | 78.3 | 19.9747
Lambsheim - Weingarten LAMBSH W | 11T0-0000-0689-D | Amprion GmbH | Lambsheim | Weingarten | 400 | [8 empty] | 3150 | 0.866 | 7.993 | 139.5 | 31.887
Lechhausen - Meitingen LECHHA W | 11T0-0000-0723-D | Amprion GmbH | Lechhausen | Meitingen | 400 | [8 empty] | 2720 | 0.841 | 7.886 | 133.2 | 30.9494
Linde - Opladen LEICHL O | 11T0-0000-0791-S | Amprion GmbH | Linde | Opladen | 400 | [8 empty] | 2720 | 0.772 | 7.128 | 124.6 | 28.4586
Halfeshof - Opladen LEICHL W | 11T0-0000-0790-V | Amprion GmbH | Halfeshof | Opladen | 400 | [8 empty] | 2720 | 0.46 | 4.234 | 74.2 | 16.9258
Dauersberg - Siegburg LEUSHD N | 11T0-0000-0212-8 | Amprion GmbH | Dauersberg | Siegburg | 220 | [6 empty] | 1290 |  |  | 3.031 | 16.03 | 183.2 | 51.7489
Dauersberg - Siegburg LEUSHD S | 11T0-0000-0213-5 | Amprion GmbH | Dauersberg | Siegburg | 220 | [6 empty] | 1290 |  |  | 3.031 | 16.03 | 183.2 | 51.7489
Liessem - Sechtem LIESSM O | 11T0-0000-0842-3 | Amprion GmbH | Liessem | Sechtem | 400 | [8 empty] | 2580 | 0.99 | 8.81 | 150.2 | 34.7372
Dauersberg - Limburg LIMBG W | 11T0-0000-1515-F | Amprion GmbH | Dauersberg | Limburg | 400 | [6 empty] | 2720 |  |  | 1.264 | 11.86 | 200.1 | 46.5197
Kusenhorst - Niederrhein LIPPE N | 11T0-0000-0680-3 | Amprion GmbH | Kusenhorst | Niederrhein | 400 | [8 empty] | 3096 | 1.026 | 9.514 | 158.9 | 37.1291
Y-Kusenhorst (-Niederrhein - Nordlicht) LIPPE S | 11T0-0000-1535-7 | Amprion GmbH | Kusenhorst | Y-Kusenhorst | 400 | [6 empty] | 2580 |  |  | 0.31 | 2.77 | 46.1 | 10.791
Y-Nordlicht (-Kusenhorst - Niederrhein) LIPPE S | 11T0-0000-1537-1 | Amprion GmbH | Nordlicht | Y-Kusenhorst | 400 | [6 empty] | 2720 |  |  | 0.35 | 3.48 | 52.2 | 12.8705
Y-Niederrhein (-Kusenhorst - Nordlicht) LIPPE S | 11T0-0000-1536-4 | Amprion GmbH | Niederrhein | Y-Kusenhorst | 400 | [6 empty] | 2720 |  |  | 0.72 | 6.65 | 116.2 | 26.5452
Spellen - Walsum LOENEN O | 11T0-0000-0491-6 | Amprion GmbH | Spellen | Walsum | 220 | [6 empty] | 1360 |  |  | 0.741 | 4.058 | 51.6 | 13.8182
Spellen - Walsum LOENEN W | 11T0-0000-0492-3 | Amprion GmbH | Spellen | Walsum | 220 | [6 empty] | 1360 |  |  | 0.744 | 4.007 | 50.7 | 13.6108
Utfort - Walsum LOHHEI W | 11T0-0000-0890-Q | Amprion GmbH | Utfort | Walsum | 400 | [6 empty] | 2580 |  |  | 0.271 | 2.453 | 39.3 | 9.376
Osterath - Rath MEERBU W | 11T0-0000-1498-G | Amprion GmbH | Osterath | Rath | 400 | [6 empty] | 646 |  |  | 0.629 | 5.908 | 99.5 | 23.1528
Gundelfingen - Meitingen MEITGN S | 11T0-0000-0722-G | Amprion GmbH | Gundelfingen | Meitingen | 400 | [6 empty] | 2720 |  |  | 1.081 | 9.98 | 171.1 | 39.4604
Gundelfingen - Meitingen MEITGN N | 11T0-0000-0721-J | Amprion GmbH | Gundelfingen | Meitingen | 400 | [6 empty] | 2720 |  |  | 1.081 | 9.98 | 171.1 | 39.4604
Gersteinwerk - Mengede MENGED N | 11T0-0000-0729-W | Amprion GmbH | Gersteinwerk | Mengede | 400 | [8 empty] | 3150 | 0.955 | 8.765 | 150.9 | 34.729
Lippe - Mengede MENGED S | 11T0-0000-0733-9 | Amprion GmbH | Lippe | Mengede | 400 | [8 empty] | 3150 | 0.282 | 2.595 | 45.3 | 10.3535
Hanekenfaehr - Meppen MEPPEN | 11T0-0000-0640-J | Amprion GmbH | Hanekenfaehr | Meppen | 400 | [8 empty] | 3150 | 1.304 | 11.93 | 205.5 | 47.2822
Duennwald - Gremberghoven MERHM O | 11T0-0000-0234-V | Amprion GmbH | Duennwald | Gremberghoven | 220 | [8 empty] | 1506 | 0.668 | 3.684 | 39.8 | 11.5631
Duennwald - Gremberghoven MERHM W | 11T0-0000-0235-S | Amprion GmbH | Duennwald | Gremberghoven | 220 | [8 empty] | 1506 | 0.668 | 3.684 | 39.8 | 11.5631
Koblenz - Weissenthurm METTER | 11T0-0000-0898-2 | Amprion GmbH | Koblenz | Weissenthurm | 400 | [6 empty] | 2580 |  |  | 0.472 | 4.534 | 68.8 | 16.8658
Sechtem - Weissenthurm MITREI | 11T0-0000-0844-Y | Amprion GmbH | Sechtem | Weissenthurm | 400 | [6 empty] | 2580 |  |  | 1.827 | 15.85 | 271.7 | 62.6658
Muendelheim - Utfort MUENDL N | 11T0-0000-0370-M | Amprion GmbH | Muendelheim | Utfort | 220 | [8 empty] | 1846 | 0.809 | 5.801 | 93.6 | 22.2516
Muendelheim - Uerdingen MUENDL S | 11T0-0000-0368-2 | Amprion GmbH | Muendelheim | Uerdingen | 220 | [6 empty] | 1360 |  |  | 0.477 | 2.55 | 33.6 | 8.8392
Amelsbueren - Muenster MUNSTR O | 11T0-0000-0124-3 | Amprion GmbH | Amelsbueren | Muenster | 220 | [6 empty] | 1004 |  |  | 0.209 | 1.081 | 12.8 | 3.5521
Y-Hanekenfaehr (-Kottigerhook - Kusenhorst) MUENST | 11T0-0000-0643-A | Amprion GmbH | Hanekenfaehr | Y-Hanekenfaehr | 400 | [8 empty] | 2872 | 1.477 | 13.56 | 203.3 | 50.1383
Y-Kottigerhook (-Hanekenfaehr - Kusenhorst) MUENST | 11T0-0000-0669-L | Amprion GmbH | Kottigerhook | Y-Hanekenfaehr | 400 | [8 empty] | 2872 | 0.005 | 0.05 | 0.4 | 0.13505
Y-Kusenhorst (-Hanekenfaehr - Kottigerhook) MUENST | 11T0-0000-0684-S | Amprion GmbH | Kusenhorst | Y-Hanekenfaehr | 400 | [8 empty] | 2872 | 1.784 | 16.34 | 245.8 | 60.5185
Diefflen - Saarwellingen NALBA O | 11T0-0000-0223-1 | Amprion GmbH | Diefflen | Saarwellingen | 220 | [6 empty] | 581 |  |  | 0.057 | 0.331 | 3.7 | 1.0568
Diefflen - Saarwellingen NALBA W | 11T0-0000-0224-Z | Amprion GmbH | Diefflen | Saarwellingen | 220 | [6 empty] | 581 |  |  | 0.11 | 0.477 | 3.7 | 1.2686
Koblenz - Limburg NASSAU | 11T0-0000-0666-U | Amprion GmbH | Koblenz | Limburg | 400 | [6 empty] | 2720 |  |  | 1.429 | 13.53 | 224 | 52.5708
Sechtem - Weissenthurm NETTE O | 11T0-0000-0477-X | Amprion GmbH | Sechtem | Weissenthurm | 220 | [8 empty] | 1632 | 1.686 | 15.66 | 279.7 | 63.1995
Meckenheim - Weissenthurm NETTE W | 11T0-0000-0717-5 | Amprion GmbH | Meckenheim | Weissenthurm | 400 | [8 empty] | 2720 | 1.117 | 10.23 | 182 | 41.2045
Niederrhein - Walsum NRHEIN W | 11T0-0000-0750-A | Amprion GmbH | Niederrhein | Walsum | 400 | [6 empty] | 2720 |  |  | 0.519 | 4.78 | 83.5 | 19.0778
Wehrendorf - Westerkappeln NSACHS N | 11T0-0000-0891-N | Amprion GmbH | Wehrendorf | Westerkappeln | 400 | [6 empty] | 2565 |  |  | 1.69 | 15.65 | 270.9 | 62.1775
Hanekenfaehr - Wehrendorf NSACHS S | 11T0-0000-0641-G | Amprion GmbH | Hanekenfaehr | Wehrendorf | 400 | [6 empty] | 2720 |  |  | 2.034 | 18.83 | 325.9 | 74.8064
Niederstedem - Quint NSTEDM O | 11T0-0000-0390-E | Amprion GmbH | Niederstedem | Quint | 220 | [8 empty] | 2000 | 1.466 | 7.745 | 99.9 | 26.5622
Niederstedem - Trier NSTEDM W | 11T0-0000-0391-B | Amprion GmbH | Niederstedem | Trier | 220 | [8 empty] | 1290 | 1.285 | 6.959 | 87.6 | 23.5775
Ibbenbueren - Westerkappeln NIKE S | 11T0-0000-0545-9 | Amprion GmbH | Ibbenbueren | Westerkappeln | 220 | [7 empty] | 631 | 740 | 1.181 | 5.208 | 37.6 | 13.3629
Niederstedem - Rommersheim NIMSTA O | 11T0-0000-1631-E | Amprion GmbH | Niederstedem | Rommersheim | 400 | [8 empty] | 3096 | 1.01 | 8.7 | 150.4 | 34.5426
Norf - St. Peter NORF W | 11T0-0000-0496-S | Amprion GmbH | Norf | St Peter | 220 | [8 empty] | 1548 | 0.192 | 1.05 | 11.1 | 3.2601
Meitingen - Oberbachern OBACHE N | 11T-D2-D7-000504 | Amprion GmbH | Meitingen | Oberbachern | 400 | [6 empty] | 2400 |  |  | 0.538 | 6.23 | 113 | 25.337
Meitingen - Oberbachern OBACHE S | 11T-D2-D7-000512 | Amprion GmbH | Meitingen | Oberbachern | 400 | [6 empty] | 2400 |  |  | 0.538 | 6.23 | 113 | 25.337
Y-Mettmann (-Ohligs - St Peter) OERKHS W | 11T0-0000-1849-D | Amprion GmbH | Mettmann | Y-Ohligs | 400 | [7 empty] | 2580 | 3096 | 0.25 | 2.37 | 40.6 | 9.3672 | German internal tie-line
Y-Eiberg (-Ohligs - Opladen) OERKHS O | 11T0-0000-1485-T | Amprion GmbH | Eiberg | Y-Ohligs | 400 | [8 empty] | 3096 | 1.03 | 9.86 | 170.8 | 39.1881
Y-Ohligs (-Eiberg - Opladen) OERKHS O | 11T0-0000-1486-Q | Amprion GmbH | Ohligs | Y-Ohligs | 400 | [8 empty] | 3096 | 0.01 | 0.08 | 1.5 | 0.3308
Y-Opladen (-Eiberg - Ohligs) OERKHS O | 11T0-0000-1487-N | Amprion GmbH | Opladen | Y-Ohligs | 400 | [8 empty] | 3150 | 0.47 | 4.52 | 77.5 | 17.8728
Y-Ohligs (-Mettmann - St Peter) OERKHS W | 11T0-0000-1851-X | Amprion GmbH | Ohligs | Y-Ohligs | 400 | [7 empty] | 2580 | 3096 | 0.01 | 0.08 | 1.5 | 0.3308 | German internal tie-line
Y-St Peter (-Ohligs - Mettmann) OERKHS W | 11T0-0000-1852-U | Amprion GmbH | St Peter | Y-Ohligs | 400 | [7 empty] | 2580 | 3096 | 0.54 | 5.32 | 85.6 | 20.3781 | German internal tie-line
Bollenacker - Sechtem OLEFIN W | 11T0-0000-1864-K | Amprion GmbH | Bollenacker | Sechtem | 220 | [6 empty] | 1290 |  |  | 0.275 | 2.547 | 54.3 | 11.2302
Opladen - Rommerskirchen OPLADN N | 11T0-0000-0793-M | Amprion GmbH | Opladen | Rommerskirchen | 400 | [8 empty] | 2580 | 0.628 | 5.582 | 97 | 22.2204
Opladen - Rommerskirchen OPLADN S | 11T0-0000-0794-J | Amprion GmbH | Opladen | Rommerskirchen | 400 | [8 empty] | 2580 | 0.628 | 5.585 | 97.1 | 22.2378 | German internal tie-line
Quint - Uchtelfangen OSBURG | 11T0-0000-0445-E | Amprion GmbH | Quint | Uchtelfangen | 220 | [8 empty] | 1539 | 3.905 | 20.86 | 273.2 | 72.089
Guetersloh - Hesseln OSNING O | 11T0-0000-1865-H | Amprion GmbH | Guetersloh | Hesseln | 400 | [6 empty] | 481 |  |  | 0.251 | 5.244 | 84.4 | 20.0897
Y-Homburg (-Mutterstadt - Uchtelfangen) OTTERB S | 11T0-0000-0326-O | Amprion GmbH | Homburg | Y-Homburg | 220 | [8 empty] | 1128 | 0.005 | 0.05 | 0.4 | 0.13505
Y-Mutterstadt (-Homburg - Uchtelfangen) OTTERB S | 11T0-0000-1436-9 | Amprion GmbH | Mutterstadt | Y-Homburg | 220 | [8 empty] | 1128 | 5.791 | 31.39 | 395.3 | 106.3728
Y-Uchtelfangen (-Homburg - Mutterstadt) OTTERB S | 11T0-0000-0505-P | Amprion GmbH | Uchtelfangen | Y-Homburg | 220 | [8 empty] | 1128 | 1.763 | 9.039 | 116.9 | 31.0412
Paffendorf - Rommerskirchen PAFFEN N | 11T0-0000-0829-R | Amprion GmbH | Paffendorf | Rommerskirchen | 400 | [8 empty] | 3150 | 0.359 | 3.285 | 56.6 | 13.0211
Paffendorf - Rommerskirchen PAFFEN S | 11T0-0000-0830-D | Amprion GmbH | Paffendorf | Rommerskirchen | 400 | [8 empty] | 3150 | 0.359 | 3.273 | 56.8 | 13.0202
Kruckel - Witten PERSEBEK | 11T0-0000-0678-K | Amprion GmbH | Kruckel | Witten | 400 | [8 empty] | 3078 | 0.252 | 2.135 | 37.9 | 8.5899
St. Peter - Rommerskirchen PETER S | 11T0-0000-0856-O | Amprion GmbH | St Peter | Rommerskirchen | 400 | [6 empty] | 2720 |  |  | 0.492 | 4.728 | 76.7 | 18.1848 | German internal tie-line
Niederrhein - Pfalzdorf PFALZD N | 11T0-0000-0385-3 | Amprion GmbH | Niederrhein | Pfalzdorf | 220 | [6 empty] | 820 |  |  | 2.355 | 11.17 | 189.4 | 43.9226
Niederrhein - Pfalzdorf PFALZD S | 11T0-0000-0386-0 | Amprion GmbH | Niederrhein | Pfalzdorf | 220 | [6 empty] | 820 |  |  | 2.335 | 12.28 | 173.3 | 44.0524 | German internal tie-line
Y-Hattingen (-Laer - Poeppinghausen) POEPPI O | 11T0-0000-0320-5 | Amprion GmbH | Hattingen | Y-Kruckel | 220 | [6 empty] | 1290 |  |  | 1.054 | 5.39 | 67.2 | 18.174
Y-Laer (-Hattingen - Poeppinghausen) POEPPI O | 11T0-0000-0351-R | Amprion GmbH | Laer | Y-Kruckel | 220 | [6 empty] | 1290 |  |  | 0.025 | 0.13 | 1.5 | 0.42169
Y-Poeppinghausen (-Hattingen - Laer) POEPPI O | 11T0-0000-0444-H | Amprion GmbH | Poeppinghausen | Y-Kruckel | 220 | [6 empty] | 1290 |  |  | 0.764 | 3.853 | 48.3 | 13.027
Laer - Poeppinghausen POEPPI W | 11T0-0000-0347-D | Amprion GmbH | Laer | Poeppinghausen | 220 | [6 empty] | 1290 |  |  | 0.746 | 3.745 | 47.2 | 12.696
Y-Bergmannsglueck (-Bellendorf - Kusenhorst) POLSUM S | 11T0-0000-0170-W | Amprion GmbH | Bergmannsglueck | Y-Bellendorf | 220 | [8 empty] | 1920 | 0.039 | 0.373 | 5.4 | 1.3553
Y-Kusenhorst (-Bellendorf - Bergmannsglück) POLSUM S | 11T0-0000-0346-G | Amprion GmbH | Kusenhorst | Y-Bellendorf | 220 | [8 empty] | 1920 | 0.389 | 2.931 | 41.2 | 10.4937
Hoheneck - Pulverdingen HO PU WS | 11T-D4-D7-00014N | Amprion GmbH | Hoheneck | Pulverdingen | 400 | [9 empty] | 0.132 | 1.743 | 27.2 | 6.5751
Mittelbexbach - Otterbach RAMSTE S | 11T0-0000-0806-7 | Amprion GmbH | Mittelbexbach | Otterbach | 400 | [8 empty] | 3096 | 1.194 | 10.19 | 177 | 40.5551
Ratsbusch - Wambel RA WA N | 11T0-0000-0531-P | Amprion GmbH | Ratsbusch | Wambel | 220 | [9 empty] | 0.105 | 0.583 | 5.9 | 1.7711
Ratsbusch - Wambel RA WA S | 11T0-0000-1438-3 | Amprion GmbH | Ratsbusch | Wambel | 220 | [9 empty] | 0.105 | 0.583 | 5.9 | 1.7711
Emscherbruch - Mengede RECKLI N | 11T0-0000-1496-M | Amprion GmbH | Emscherbruch | Mengede | 400 | [8 empty] | 2580 | 0.427 | 3.853 | 64.9 | 15.1006
Buerstadt - Hoheneck REINAU O | 11T0-0000-1669-F | Amprion GmbH | Buerstadt | Hoheneck | 220 | [7 empty] | 1070 | 1282 | 6.96 | 37.53 | 410.7 | 118.5559
Opladen - St. Peter RHFELD | 11T0-0000-1671-Z | Amprion GmbH | Opladen | St Peter | 400 | [6 empty] | 2720 |  |  | 0.458 | 4.527 | 72.8 | 17.3357
Buerstadt - Pfungstadt RIED O | 11T0-0000-0816-3 | Amprion GmbH | Buerstadt | Pfungstadt | 400 | [8 empty] | 3096 | 0.803 | 7.849 | 132.4 | 30.7838
Y-Bischofsheim (-Buerstadt - Pfungstadt) RIED W | 11T0-0000-0563-7 | Amprion GmbH | Bischofsheim | Y-Pfungstadt | 400 | [8 empty] | 3150 | 0.666 | 6.539 | 109.1 | 25.5058
Y-Buerstadt (-Bischofsheim - Pfungstadt) RIED W | 11T0-0000-0573-3 | Amprion GmbH | Buerstadt | Y-Pfungstadt | 400 | [8 empty] | 3150 | 0.796 | 7.832 | 130.1 | 30.4822
Y-Pfungstadt (-Bischofsheim - Buerstadt) RIED W | 11T0-0000-0819-V | Amprion GmbH | Pfungstadt | Y-Pfungstadt | 400 | [8 empty] | 3150 | 0.009 | 0.079 | 1.4 | 0.31758
Brauweiler - Rommerskirchen ROKI O | 11T0-0000-0458-1 | Amprion GmbH | Brauweiler | Rommerskirchen | 220 | [8 empty] | 2052 | 0.424 | 3.415 | 43.1 | 11.5852
Y-Hanekenfaehr (-Oechtel - Roxel) ROXEL O | 11T0-0000-0930-8 | Amprion GmbH | Hanekenfaehr | Y-Oechtel | 400 | [8 empty] | 3078 | 0.571 | 4.887 | 84.2 | 19.3708
Y-Oechtel (-Hanekenfaehr - Roxel) ROXEL O | 11T0-0000-0931-5 | Amprion GmbH | Oechtel | Y-Oechtel | 400 | [8 empty] | 820 | 0.006 | 0.064 | 1.4 | 0.28584
Y-Roxel (-Hanekenfaehr - Oechtel) ROXEL O | 11T0-0000-0932-2 | Amprion GmbH | Roxel | Y-Oechtel | 400 | [8 empty] | 3078 | 1.491 | 12.78 | 222.7 | 50.9445
Eiberg - Mettmann RUHRTL W | 11T0-0000-1846-M | Amprion GmbH | Eiberg | Mettmann | 400 | [9 empty] | 0.78 | 7.5 | 130.6 | 29.8864
Nehden - Uentrop SAUERL N | 11T0-0000-0744-2 | Amprion GmbH | Nehden | Uentrop | 400 | [6 empty] | 2565 |  |  | 3.381 | 29.28 | 499.7 | 115.5079
Arpe - Nehden SAUERL S | 11T0-0000-0743-5 | Amprion GmbH | Arpe | Nehden | 400 | [6 empty] | 2565 |  |  | 1.498 | 12.93 | 220.8 | 51.0235
Bergmannsglueck - Niederrhein SHERMB N | 11T0-0000-0166-I | Amprion GmbH | Bergmannsglueck | Niederrhein | 220 | [6 empty] | 1360 |  |  | 1.757 | 10.02 | 115.9 | 32.5422
FWH-S - Urberach SHWANH O | 11T0-0000-0516-I | Amprion GmbH | FWH-S | Urberach | 220 | [8 empty] | 551 | 2.597 | 12.6 | 372 | 65.3775
FWH-S - Urberach SHWANH W | 11T0-0000-0517-F | Amprion GmbH | FWH-S | Urberach | 220 | [8 empty] | 551 | 2.608 | 12.65 | 357.4 | 64.2087
Kruckel - Unna SHWERT N | 11T0-0000-0548-0 | Amprion GmbH | Kruckel | Unna | 400 | [6 empty] | 3078 |  |  | 0.374 | 7.098 | 132.1 | 29.2409
Y-Oberzier (-Paffendorf - Sechtem) SECHTM N | 11T0-0000-0781-W | Amprion GmbH | Oberzier | Y-Paffendorf | 400 | [8 empty] | 3150 | 0.434 | 4.009 | 70 | 15.997
Y-Oberzier (-Paffendorf - Sechtem) SECHTM S | 11T0-0000-0782-T | Amprion GmbH | Oberzier | Y-Paffendorf | 400 | [8 empty] | 3150 | 0.434 | 4.009 | 70 | 15.997
Y-Paffendorf (-Oberzier - Sechtem) SECHTM N | 11T0-0000-0814-9 | Amprion GmbH | Paffendorf | Y-Paffendorf | 400 | [8 empty] | 3150 | 0.287 | 2.682 | 47.6 | 10.7896
Y-Paffendorf (-Oberzier - Sechtem) SECHTM S | 11T0-0000-0815-6 | Amprion GmbH | Paffendorf | Y-Paffendorf | 400 | [8 empty] | 3150 | 0.287 | 2.682 | 47.6 | 10.7896
Y-Sechtem (-Oberzier - Paffendorf) SECHTM S | 11T0-0000-0849-J | Amprion GmbH | Sechtem | Y-Paffendorf | 400 | [8 empty] | 3150 | 0.789 | 7.3 | 126.4 | 29.0072
Y-Sechtem (-Oberzier - Paffendorf) SECHTM N | 11T0-0000-0848-M | Amprion GmbH | Sechtem | Y-Paffendorf | 400 | [8 empty] | 3150 | 0.789 | 7.269 | 126.9 | 29.0028
Y-Oberzier (-Dahlem - Rommersheim) SELHN O | 11T0-0000-0783-Q | Amprion GmbH | Oberzier | Y-Dahlem | 400 | [8 empty] | 2770 | 1.784 | 15.24 | 264.1 | 60.5826
Y-Rommersheim (-Dahlem - Oberzier) SELHN O | 11T0-0000-1629-V | Amprion GmbH | Rommersheim | Y-Dahlem | 400 | [8 empty] | 3096 | 0.71 | 6.09 | 105.4 | 24.1936
Y-Niederstedem (-Dahlem - Oberzier) SELHN W | 11T0-0000-0762-0 | Amprion GmbH | Niederstedem | Y-Dahlem | 400 | [8 empty] | 2770 | 1.703 | 14.68 | 253.7 | 58.2767
Y-Oberzier (-Dahlem - Niederstedem) SELHN W | 11T0-0000-0784-N | Amprion GmbH | Oberzier | Y-Dahlem | 400 | [8 empty] | 2770 | 1.784 | 15.24 | 264.2 | 60.5941
Bechterdissen - Guetersloh SENNE N2 | 11T0-0000-0072-V | Amprion GmbH | Guetersloh | Bechterdissen | 400 | [6 empty] | 2720 |  |  | 0.345 | 3.257 | 59.8 | 13.327
Bechterdissen - Guetersloh SENNE S1 | 11T-D2-D7-00257J | Amprion GmbH | Guetersloh | Bechterdissen | 400 | [6 empty] | 2720 |  |  | 0.345 | 3.257 | 59.8 | 13.327
Y-Altenkleusheim (-Eiserfeld - Setzer Wiese) SETZE N | 11T0-0000-1441-K | Amprion GmbH | Altenkleusheim | Y-Setzer Wiese | 220 | [8 empty] | 740 | 0.687 | 2.938 | 20.1 | 7.3383
Y-Eiserfeld (-Altenkleusheim - Setzer Wiese) SETZE N | 11T0-0000-1442-H | Amprion GmbH | Eiserfeld | Y-Setzer Wiese | 220 | [8 empty] | 740 | 1.436 | 6.377 | 63 | 19.1403
Y-Setzer Wiese (-Altenkleusheim - Eiserfeld) SETZE N | 11T0-0000-1443-E | Amprion GmbH | Setzer Wiese | Y-Setzer Wiese | 220 | [8 empty] | 1360 | 0.316 | 1.692 | 22.1 | 5.8394
Dauersberg - Sechtem SIEGTA N | 11T0-0000-0586-R | Amprion GmbH | Dauersberg | Sechtem | 400 | [6 empty] | 2720 |  |  | 1.86 | 17.2 | 298.2 | 68.3895
Dauersberg - Sechtem SIEGTA S | 11T0-0000-0587-O | Amprion GmbH | Dauersberg | Sechtem | 400 | [6 empty] | 2720 |  |  | 1.86 | 17.2 | 298.2 | 68.3895
Bacharach - Weissenthurm SOONWD O | 11T0-0000-0973-K | Amprion GmbH | Bacharach | Weissenthurm | 400 | [8 empty] | 3096 | 1.449 | 12.62 | 218 | 50.0875
Waldlaubersheim - Weissenthurm SOONWD W | 11T0-0000-0901-H | Amprion GmbH | Waldlaubersheim | Weissenthurm | 400 | [8 empty] | 3096 | 1.911 | 16.49 | 285.2 | 65.4872
Niederrhein - Spellen SPELLN S | 11T0-0000-0387-Y | Amprion GmbH | Niederrhein | Spellen | 220 | [6 empty] | 1360 |  |  | 0.404 | 2.17 | 28.5 | 7.5097
Y-Brauweiler (-Opladen - Rommerskirchen) STOMM N | 11T0-0000-1866-E | Amprion GmbH | Brauweiler | Y-Rommerskirchen | 220 | [6 empty] | 1300 |  |  | 0.152 | 2.662 | 53.5 | 11.396
Y-Opladen (-Brauweiler - Rommerskirchen) STOMM N | 11T0-0000-1867-B | Amprion GmbH | Opladen | Y-Rommerskirchen | 220 | [6 empty] | 1290 |  |  | 1.321 | 7.386 | 83.1 | 23.6579
Y-Rommerskirchen (-Brauweiler - Opladen) STOMM N | 11T0-0000-1869-5 | Amprion GmbH | Rommerskirchen | Y-Rommerskirchen | 220 | [6 empty] | 1380 |  |  | 0.005 | 0.05 | 0.4 | 0.13505
Fuehlingen - Rommerskirchen STOMM S | 11T0-0000-0267-A | Amprion GmbH | Fuehlingen | Rommerskirchen | 220 | [8 empty] | 1360 | 1.024 | 5.516 | 71.8 | 19.004
Gellep - Muendelheim STRATM W | 11T0-0000-0364-E | Amprion GmbH | Gellep | Muendelheim | 220 | [6 empty] | 1290 |  |  | 0.315 | 1.655 | 21.8 | 5.7359
Norf - St. Peter STUERZ O | 11T0-0000-1445-8 | Amprion GmbH | Norf | St Peter | 220 | [6 empty] | 2052 |  |  | 0.096 | 0.542 | 21.8 | 3.2825
Norf - St. Peter STUERZ W | 11T0-0000-0497-P | Amprion GmbH | Norf | St Peter | 220 | [8 empty] | 1632 | 0.172 | 0.958 | 11.7 | 3.197
Ensdorf - Uchtelfangen TAUBNT N | 11T0-0000-0604-N | Amprion GmbH | Ensdorf | Uchtelfangen | 400 | [6 empty] | 2720 |  |  | 0.64 | 5.887 | 103.2 | 23.5374
Ensdorf - Uchtelfangen TAUBNT S | 11T0-0000-0605-K | Amprion GmbH | Ensdorf | Uchtelfangen | 400 | [6 empty] | 2720 |  |  | 0.64 | 5.888 | 103.2 | 23.5394
Kriftel - Frankfurt TAUNUS 2 | 11T0-0000-0030-G | Amprion GmbH | Kriftel | Frankfurt | 400 | [6 empty] | 2760 |  |  | 0.13 | 1.395 | 19.4 | 4.9677
Herbertingen - Tiengen TIENGN N | 11T-D4-D7-00010V | Amprion GmbH | Tiengen | Herbertingen | 400 | [6 empty] | 1792 |  |  | 1.97 | 17.82 | 196.9 | 56.565
Y-Osterath (-Selbeck - Utfort) TOESEE W | 11T0-0000-0805-A | Amprion GmbH | Osterath | Y-Osterath | 400 | [6 empty] | 2720 |  |  | 0.451 | 3.65 | 70.8 | 15.3509
Y-Selbeck (-Osterath - Utfort) TOESEE W | 11T0-0000-0851-2 | Amprion GmbH | Selbeck | Y-Osterath | 400 | [6 empty] | 615 |  |  | 0.406 | 3.992 | 65.4 | 15.4296
Y-Utfort (-Osterath - Selbeck) TOESEE W | 11T0-0000-0880-U | Amprion GmbH | Utfort | Y-Osterath | 400 | [6 empty] | 2720 |  |  | 0.632 | 8.621 | 101.5 | 28.2477
Bischofsheim - Kriftel TREBUR S | 11T0-0000-0670-7 | Amprion GmbH | Bischofsheim | Kriftel | 400 | [6 empty] | 2500 |  |  | 0.515 | 5.169 | 76.1 | 18.9394
Kelsterbach - Kriftel TREBUR N | 11T0-0000-0671-4 | Amprion GmbH | Kelsterbach | Kriftel | 400 | [6 empty] | 2720 |  |  | 0.371 | 3.547 | 70.4 | 15.09
Sechtem - Siegburg TROISD O | 11T0-0000-0486-W | Amprion GmbH | Sechtem | Siegburg | 220 | [8 empty] | 1360 | 1.004 | 5.289 | 61 | 17.1523
Sechtem - Siegburg TROISD W | 11T0-0000-0487-T | Amprion GmbH | Sechtem | Siegburg | 220 | [8 empty] | 1360 | 1.004 | 5.317 | 60.6 | 17.1412
Nehden - Twistetal TWIST O3 | 11T-D2-D7-00010G | Amprion GmbH | Nehden | Twistetal | 400 | [6 empty] | 2580 |  |  | 0.47 | 4.438 | 75.9 | 17.5261
Nehden - Twistetal TWIST W4 | 11T-D2-D7-00011E | Amprion GmbH | Nehden | Twistetal | 400 | [6 empty] | 2580 |  |  | 0.47 | 4.438 | 75.9 | 17.5261
Osburg - Uchtelfangen UCHTLF O | 11T0-0000-0798-7 | Amprion GmbH | Osburg | Uchtelfangen | 400 | [6 empty] | 2580 |  |  | 1.449 | 12.34 | 214.6 | 49.141
Niederstedem - Uchtelfangen UCHTLF W | 11T0-0000-0756-T | Amprion GmbH | Niederstedem | Uchtelfangen | 400 | [6 empty] | 2580 |  |  | 2.802 | 23.99 | 415.7 | 95.3623
Y-Gersteinwerk (-Hanekenfaehr - Uentrop) UENTRO N | 11T0-0000-0616-D | Amprion GmbH | Gersteinwerk | Y-Gersteinwerk | 400 | [7 empty] | 2720 | 3078 | 0.339 | 3.131 | 54.3 | 12.4512
Y-Hanekenfaehr (-Gersteinwerk - Uentrop) UENTRO N | 11T0-0000-0644-7 | Amprion GmbH | Hanekenfaehr | Y-Gersteinwerk | 400 | [7 empty] | 2368 | 2844 | 2.891 | 26.27 | 449.9 | 103.8148
Y-Uentrop (-Gersteinwerk - Hanekenfaehr) UENTRO N | 11T0-0000-0869-B | Amprion GmbH | Uentrop | Y-Gersteinwerk | 400 | [7 empty] | 2720 | 3078 | 0.405 | 3.767 | 64.6 | 14.8965
Roxel - Uentrop UENTRO S | 11T0-0000-0840-9 | Amprion GmbH | Roxel | Uentrop | 400 | [8 empty] | 3078 | 1.656 | 14.25 | 246.7 | 56.6192
Uerdingen - Utfort UERDIN W | 11T0-0000-0113-A | Amprion GmbH | Uerdingen | Utfort | 220 | [8 empty] | 1160 | 0.875 | 4.693 | 48.3 | 14.3771
Grosskrotzenburg - Urberach UMAIN N2 | 11T-D2-D7-000318 | Amprion GmbH | Urberach | Großkrotzenburg | 400 | [6 empty] | 2720 |  |  | 0.322 | 2.97 | 51.7 | 11.833
Dettingen - Grosskrotzenburg UMAIN S1 | 11T-D2-D7-00030A | Amprion GmbH | Dettingen | Großkrotzenburg | 400 | [6 empty] | 2720 |  |  | 0.06 | 0.562 | 9.8 | 2.2411
Y-Duelken (-Edelstahl - Utfort) UTFORT W | 11T0-0000-1446-5 | Amprion GmbH | Duelken | Y-Edelstahl | 220 | [6 empty] | 1360 |  |  | 0.628 | 5.761 | 100.1 | 22.9318
Y-Edelstahl (-Duelken - Utfort) UTFORT W | 11T0-0000-1447-2 | Amprion GmbH | Edelstahl | Y-Edelstahl | 220 | [6 empty] | 1360 |  |  | 0.201 | 1.006 | 13.1 | 3.4666
Y-Utfort (-Duelken - Edelstahl) UTFORT W | 11T0-0000-1449-X | Amprion GmbH | Utfort | Y-Edelstahl | 220 | [7 empty] | 841 | 1031 | 1.649 | 7.817 | 65.4 | 21.5914
Rommerskirchen - Sechtem VILLE O | 11T0-0000-0831-A | Amprion GmbH | Rommerskirchen | Sechtem | 400 | [8 empty] | 3150 | 1.001 | 8.591 | 148.8 | 34.1425
Rommerskirchen - Sechtem VILLE W | 11T0-0000-1011-F | Amprion GmbH | Rommerskirchen | Sechtem | 400 | [8 empty] | 3096 | 0.989 | 8.594 | 148.9 | 34.1599
Voehringen - Woringen VOEHRG O | 11T0-0000-0883-L | Amprion GmbH | Voehringen | Woringen | 400 | [6 empty] | 2760 |  |  | 1.237 | 11.93 | 207 | 47.4544
Knapsack - Sechtem WABERG W | 11T0-0000-0663-2 | Amprion GmbH | Knapsack | Sechtem | 400 | [8 empty] | 3150 | 0.348 | 3.442 | 53.9 | 13.0068
Y-Walsum (-Hamborn - Schwelgern) WALSUM N | 11T0-0000-1457-Z | Amprion GmbH | Walsum | Y-Walsum | 220 | [8 empty] | 1360 | 0.088 | 0.447 | 7.9 | 1.7945 | German internal tie-line
Y-Walsum (-Hamborn - Schwelgern) WALSUM S | 11T0-0000-0529-5 | Amprion GmbH | Walsum | Y-Schwelgern | 220 | [9 empty] | 0.083 | 0.461 | 5.5 | 1.5206 | German internal tie-line
Y-Hamborn (-Schwelgern - Walsum) WALSUM N | 11T0-0000-1455-4 | Amprion GmbH | Hamborn | Y-Walsum | 220 | [8 empty] | 1360 | 0.256 | 1.379 | 17.8 | 4.7311
Y-Schwelgern (-Hamborn - Walsum) WALSUM N | 11T0-0000-1456-1 | Amprion GmbH | Schwelgern | Y-Walsum | 220 | [8 empty] | 700 | 0.085 | 0.464 | 5.8 | 1.5666
Y-Hamborn (-Schwelgern - Walsum) WALSUM S | 11T0-0000-0304-1 | Amprion GmbH | Hamborn | Y-Schwelgern | 220 | [9 empty] | 0.256 | 1.379 | 17.8 | 4.7311
Y-Schwelgern (-Hamborn - Walsum) WALSUM S | 11T0-0000-0471-E | Amprion GmbH | Schwelgern | Y-Schwelgern | 220 | [9 empty] | 0.099 | 0.54 | 6.8 | 1.8299
Gersteinwerk - Lippe WALTRO S | 11T0-0000-0610-V | Amprion GmbH | Gersteinwerk | Lippe | 400 | [9 empty] | 0.655 | 6.073 | 104.7 | 24.0794
Gersteinwerk - Wambel WAMBEL O | 11T0-0000-0287-2 | Amprion GmbH | Gersteinwerk | Wambel | 220 | [6 empty] | 1290 |  |  | 1.173 | 7.896 | 90.5 | 25.527
Gersteinwerk - Wambel WAMBEL W | 11T0-0000-0289-X | Amprion GmbH | Gersteinwerk | Wambel | 220 | [6 empty] | 1290 |  |  | 1.172 | 7.896 | 90.4 | 25.5129
BASF - Maximiliansau WEINGT | 11T0-0000-0359-3 | Amprion GmbH | BASF | Maximiliansau | 220 | [8 empty] | 1632 | 2.178 | 19.12 | 321.6 | 74.8813
Liessem - Weissenthurm WTHURM O | 11T0-0000-0700-U | Amprion GmbH | Liessem | Weissenthurm | 400 | [8 empty] | 2580 | 1.246 | 10.79 | 186.8 | 42.8717
Eiberg - Hattingen WEITMR W | 11T0-0000-0647-Z | Amprion GmbH | Eiberg | Hattingen | 400 | [8 empty] | 2844 | 0.672 | 6.539 | 103.4 | 24.8306 | German internal tie-line
Y-Bochum (-Hattingen - Welper) WELPER O | 11T0-0000-0184-G | Amprion GmbH | Bochum | Y-Welper | 220 | [6 empty] | 1290 |  |  | 0.191 | 1.852 | 28.3 | 6.9133
Y-Hattingen (-Bochum - Welper) WELPER O | 11T0-0000-0321-2 | Amprion GmbH | Hattingen | Y-Welper | 220 | [6 empty] | 1290 |  |  | 0.158 | 1.435 | 21.7 | 5.3288
Y-Welper (-Bochum - Hattingen) WELPER O | 11T0-0000-0542-I | Amprion GmbH | Welper | Y-Welper | 220 | [6 empty] | 1290 |  |  | 0.091 | 0.532 | 5.8 | 1.6774
Niederstedem - Wengerrohr WENGER | 11T0-0000-0394-2 | Amprion GmbH | Niederstedem | Wengerrohr | 220 | [8 empty] | 1846 | 2.362 | 11.81 | 150.7 | 40.2859
Amelsbueren - Gersteinwerk WERSE W | 11T0-0000-0281-K | Amprion GmbH | Amelsbueren | Gersteinwerk | 220 | [8 empty] | 1539 | 1.655 | 8.318 | 104.8 | 28.1943
Y-Niederrhein (-Ossenberg - Utfort) WESEL O | 11T0-0000-0389-S | Amprion GmbH | Niederrhein | Y-Ossenberg | 220 | [7 empty] | 823 | 1046 | 0.649 | 4.261 | 31.4 | 11.0457
Y-Ossenberg (-Niederrhein - Utfort) WESEL O | 11T0-0000-0423-S | Amprion GmbH | Ossenberg | Y-Ossenberg | 220 | [6 empty] | 700 |  |  | 0.296 | 1.579 | 20.9 | 5.4857
Y-Utfort (-Ossenberg - Niederrhein) WESEL O | 11T0-0000-0523-N | Amprion GmbH | Utfort | Y-Ossenberg | 220 | [7 empty] | 630 | 978 | 0.581 | 3.618 | 26.1 | 9.2795
Emscherbruch - Kusenhorst WEHOLT O | 11T0-0000-1497-J | Amprion GmbH | Emscherbruch | Kusenhorst | 400 | [8 empty] | 2844 | 0.581 | 5.297 | 87.6 | 20.5702
Luestringen - Westerkappeln WESTER N | 11T0-0000-0714-E | Amprion GmbH | Luestringen | Westerkappeln | 400 | [6 empty] | 960 |  |  | 0.495 | 4.724 | 82.9 | 18.8975 | German internal tie-line
Luestringen - Westerkappeln WESTER S | 11T0-0000-0715-B | Amprion GmbH | Luestringen | Westerkappeln | 220 | [6 empty] | 960 |  |  | 0.505 | 4.679 | 80.5 | 18.533
Dauersberg - Dillenburg WESTW O2 | 11T-D2-D7-00020D | Amprion GmbH | Dauersberg | Dillenburg | 400 | [6 empty] | 2612 |  |  | 1.072 | 9.68 | 167.2 | 38.4173
Y-Dauersberg (-Asslar - Limburg) WESTW W1 | 11T0-0000-0994-9 | Amprion GmbH | Dauersberg | Y-Dauersberg | 400 | [6 empty] | 2720 |  |  | 0.51 | 4.716 | 81.7 | 18.7443
Y-Limburg (-Asslar - Dauersberg) WESTW W1 | 11T0-0000-0995-6 | Amprion GmbH | Limburg | Y-Dauersberg | 400 | [6 empty] | 2720 |  |  | 0.755 | 7.141 | 118.3 | 27.7551
Y-Asslar (-Dauersberg - Limburg) WESTW W1 | 11T0-0000-1238-D | Amprion GmbH | Y-Dauersberg | Asslar | 400 | [6 empty] | 2612 |  |  | 0.521 | 4.571 | 78.2 | 18.0543
Y-Huellen (-Kusenhorst - Mengede) WESTFL W | 11T0-0000-0960-X | Amprion GmbH | Huellen | Y-Huellen | 400 | [8 empty] | 3096 | 0.134 | 1.161 | 20.1 | 4.613
Y-Kusenhorst (-Huellen - Mengede) WESTFL W | 11T0-0000-0959-A | Amprion GmbH | Kusenhorst | Y-Huellen | 400 | [8 empty] | 3096 | 0.52 | 4.722 | 78.4 | 18.3735
Y-Mengede (-Huellen - Kusenhorst) WESTFL W | 11T0-0000-0958-D | Amprion GmbH | Mengede | Y-Huellen | 400 | [8 empty] | 3096 | 0.497 | 4.506 | 76.8 | 17.7643
Wehrendorf - Westerkappeln WIEHEN O | 11T0-0000-0537-7 | Amprion GmbH | Wehrendorf | Westerkappeln | 220 | [6 empty] | 1360 |  |  | 3.361 | 18.19 | 233.5 | 62.2345
Mengede - Witten WITTEN W | 11T0-0000-0734-6 | Amprion GmbH | Mengede | Witten | 400 | [8 empty] | 2580 | 0.72 | 6.174 | 107.2 | 24.567 | German internal tie-line
Y-Bacharach (-Buerstadt - Waldlaubersheim) WONNEG O | 11T0-0000-0976-B | Amprion GmbH | Bacharach | Y-Waldlaubersheim | 400 | [8 empty] | 3078 | 0.443 | 3.867 | 67.1 | 15.3822
Y-Buerstadt (-Bacharach - Waldlaubersheim) WONNEG O | 11T0-0000-0977-8 | Amprion GmbH | Buerstadt | Y-Waldlaubersheim | 400 | [8 empty] | 3078 | 1.741 | 14.86 | 257.1 | 59.0244
Y-Waldlaubersheim (-Bacharach - Buerstadt) WONNEG O | 11T0-0000-0975-E | Amprion GmbH | Waldlaubersheim | Y-Waldlaubersheim | 400 | [8 empty] | 3078 | 0.005 | 0.05 | 0.4 | 0.13505 | German internal tie-line
Buerstadt - Waldlaubersheim WONNEG W | 11T0-0000-0885-F | Amprion GmbH | Buerstadt | Waldlaubersheim | 400 | [8 empty] | 3096 | 1.741 | 14.86 | 257.4 | 59.0589
Niederrhein - Utfort ZENSEN S | 11T0-0000-1534-A | Amprion GmbH | Niederrhein | Utfort | 400 | [6 empty] | 2580 |  |  | 0.79 | 7.19 | 122 | 28.2824 | German internal tie-line
Osterath - St. Peter ZONS O | 11T0-0000-1462-9 | Amprion GmbH | Osterath | St Peter | 220 | [6 empty] | 1360 |  |  | 0.758 | 7.147 | 117.8 | 27.708
Norf - Osterath ZONS W | 11T0-0000-0425-M | Amprion GmbH | Norf | Osterath | 220 | [8 empty] | 1548 | 1.73 | 9.289 | 116.6 | 31.4272 | German internal tie-line
Aschach - Hausruck 203B | 14T-220-0-0203BF | APG | Aschach | Hausruck | 220 | [6 empty] | 800 |  |  | 3.478 | 19.63 | 169.8972 | 53
Aschach - St. Peter 203A | 14T-220-0-0203AH | APG | Aschach | St. Peter | 220 | [6 empty] | 800 |  |  | 4.27 | 28.5 | 296.2836 | 84.2
Bisamberg - Duernrohr 436A | 14T-380-0-0436AJ | APG | Bisamberg | Duernrohr | 400 | [6 empty] | 2300 |  |  | 1.11 | 15.52 | 193.1136 | 51.1
Bisamberg - Duernrohr 444A | 14T-380-0-0444AL | APG | Bisamberg | Duernrohr | 400 | [6 empty] | 2300 |  |  | 1.109 | 15.52 | 193.1136 | 51.1
Bisamberg - Sarasdorf 444C | 14T-380-0-0444CH | APG | Bisamberg | Sarasdorf | 400 | [6 empty] | 2300 |  |  | 1.078 | 15.05 | 188.0871 | 49.6
Bisamberg - Duernrohr 297 | 14T-220-0-002977 | APG | Bisamberg | Duernrohr | 220 | [6 empty] | 2080 |  |  | 1.1 | 12.7 | 167.1327 | 51.1
Bisamberg - Duernrohr 298 | 14T-220-0-002985 | APG | Bisamberg | Duernrohr | 220 | [6 empty] | 2080 |  |  | 1.1 | 12.7 | 167.1327 | 51.1
Bisamberg - Kledering 228B | 14T-220-0-0228BT | APG | Bisamberg | Kledering | 220 | [6 empty] | 1200 |  |  | 2.165 | 11.71 | 137.9473 | 37.5
Bisamberg - Wien Suedost 227 | 14T-220-0-00227S | APG | Bisamberg | Wien Suedost | 220 | [6 empty] | 1200 |  |  | 2.248 | 12.14 | 143.0052 | 38.9
Bisamberg - Ybbsfeld 207 | 14T-220-0-00207Y | APG | Bisamberg | Ybbsfeld | 220 | [6 empty] | 800 |  |  | 8.876 | 47.31 | 321.699 | 114.6
Bisamberg - Ybbsfeld 208 | 14T-220-0-00208W | APG | Bisamberg | Ybbsfeld | 220 | [6 empty] | 800 |  |  | 8.876 | 47.31 | 321.699 | 114.6
Duernrohr - Etzersdorf 434B | 14T-380-0-0434BN | APG | Duernrohr | Etzersdorf | 400 | [6 empty] | 2300 |  |  | 0.3 | 4.4 | 51.0509 | 13.9
Duernrohr - Kronstorf 433 | 14T-380-0-00433L | APG | Duernrohr | Kronstorf | 400 | [6 empty] | 2300 |  |  | 2.56 | 37.2 | 434.7963 | 118.3
Duernrohr - Wien Suedost 435A | 14T-380-0-0435AM | APG | Duernrohr | Wien Suedost | 400 | [6 empty] | 2300 |  |  | 2.75 | 38.62 | 480.3494 | 127
Duernrohr - Wien Suedost 443A | 14T-380-0-0443AO | APG | Duernrohr | Wien Suedost | 400 | [6 empty] | 2300 |  |  | 2.75 | 38.62 | 480.3494 | 127
Ernsthofen - Hausruck 203C | 14T-220-0-0203CD | APG | Ernsthofen | Hausruck | 220 | [6 empty] | 1000 |  |  | 1.164 | 13.15 | 185.8569 | 45.9
Ernsthofen - Sattledt 204C | 14T-220-0-0204CA | APG | Ernsthofen | Sattledt | 220 | [6 empty] | 1070 |  |  | 0.869 | 9.823 | 138.638 | 34.2
Ernsthofen - Wallsee 205A | 14T-220-0-0205AB | APG | Ernsthofen | Wallsee | 220 | [6 empty] | 810 |  |  | 1.79 | 9.27 | 62.7376 | 22.4
Ernsthofen - Ybbsfeld 206 | 14T-221-0-00206Q | APG | Ernsthofen | Ybbsfeld | 220 | [6 empty] | 810 |  |  | 3.44 | 18.24 | 123.6215 | 44.1
Ernsthofen - Klaus 201B | 14T-220-0-0201BL | APG | Ernsthofen | Klaus | 220 | [6 empty] | 925 |  |  | 3.47 | 18 | 128.35 | 67.4
Ernsthofen - Weissenbach 202 | 14T-220-0-002027 | APG | Ernsthofen | Weissenbach | 220 | [6 empty] | 925 |  |  | 6.67 | 34.49 | 240.08 | 84.4
Etzersdorf - Kronstorf 434A | 14T-380-0-0434AP | APG | Etzersdorf | Kronstorf | 400 | [6 empty] | 2300 |  |  | 2.26 | 32.82 | 383.5884 | 0.7
Feistritz - Obersielach 268 | 14T-220-0-00268E | APG | Feistritz | Obersielach | 220 | [6 empty] | 2080 |  |  | 1.238 | 14.2 | 185.8566 | 47.8
Feistritz - Villach Süd 266C | 14T-220-0-0266CH | APG | Feistritz | Villach Süd | 220 | [6 empty] | 2080 |  |  | 0.761 | 8.727 | 114.2 | 41.3
Greuth - Lienz 266A | 14T-220-0-0266AL | APG | Greuth | Lienz | 220 | [6 empty] | 2080 |  |  | 2.111 | 24.23 | 317.2999 | 81.5
Greuth - Villach Süd 266B | 14T-220-0-0266BJ | APG | Greuth | Villach Süd | 220 | [6 empty] | 2080 |  |  | 0.308 | 3.535 | 46.28 | 81.5
Hausruck - Sattledt 204B | 14T-220-0-0204BC | APG | Hausruck | Sattledt | 220 | [6 empty] | 1000 |  |  | 0.295 | 3.33 | 47.2495 | 11.7
Hessenberg - Obersielach 286 | 14T-220-0-00286C | APG | Hessenberg | Obersielach | 220 | [6 empty] | 800 |  |  | 8.379 | 41.2 | 279.35 | 99.4
Hessenberg - Ternitz 225A | 14T-220-0-0225A3 | APG | Hessenberg | Ternitz | 220 | [6 empty] | 750 |  |  | 8.03 | 39.5 | 267.5694 | 95.2
Hessenberg - Ternitz 226A | 14T-220-0-0226A0 | APG | Hessenberg | Ternitz | 220 | [6 empty] | 750 |  |  | 8.03 | 39.5 | 267.5694 | 95.2
Hessenberg - Weissenbach 223 | 14T-221-0-00223Q | APG | Hessenberg | Weissenbach | 220 | [6 empty] | 800 |  |  | 5.99 | 29.5 | 199.8367 | 71.1
Hessenberg - Weissenbach 224 | 14T-220-0-00224Y | APG | Hessenberg | Weissenbach | 220 | [6 empty] | 800 |  |  | 5.99 | 29.5 | 199.8367 | 71.1
Hessenberg - Zeltweg 287 | 14T-220-0-00287A | APG | Hessenberg | Zeltweg | 220 | [6 empty] | 800 |  |  | 3.634 | 17.87 | 121.14 | 43.1
Jochenstein - Schaerding 237 | 14T-220-0-00237P | APG | Jochenstein | Schaerding | 220 | [6 empty] | 720 |  |  | 2.08 | 9.6 | 71.6597 | 24.5
Jochenstein - Schaerding 238 | 14T-220-0-00238N | APG | Jochenstein | Schaerding | 220 | [6 empty] | 720 |  |  | 2.08 | 9.6 | 71.6597 | 24.5
Kainachtal - Obersielach 471 | 14T-380-0-00471D | APG | Kainachtal | Obersielach | 400 | [6 empty] | 2300 |  |  | 1.56 | 22.88 | 267.2867 | 72
Kainachtal - Obersielach 472 | 14T-380-0-00472B | APG | Kainachtal | Obersielach | 400 | [6 empty] | 2300 |  |  | 1.56 | 22.88 | 267.2867 | 72
Kledering - Wien Suedost 228A | 14T-220-0-0228AV | APG | Kledering | Wien Suedost | 220 | [6 empty] | 1200 |  |  | 0.12 | 0.65 | 7.5178 | 2.1
Kronstorf - St. Peter 431 | 14T-380-0-00431P | APG | Kronstorf | St. Peter | 400 | [6 empty] | 2300 |  |  | 2.411 | 34.98 | 409.6636 | 111.3
Kronstorf - St. Peter 432 | 14T-380-0-00432N | APG | Kronstorf | St. Peter | 400 | [6 empty] | 2300 |  |  | 2.411 | 34.98 | 409.6636 | 111.3
Lienz - Tauern 451 | 14T-380-0-00451J | APG | Lienz | Tauern | 400 | [6 empty] | 2180 |  |  | 1.847 | 26.76 | 311.3631 | 85
Lienz - Tauern 452 | 14T-380-0-00452H | APG | Lienz | Tauern | 400 | [6 empty] | 2180 |  |  | 1.85 | 26.8 | 311.6145 | 85
Lienz - Villach Süd 267A | 14T-220-0-0267AI | APG | Lienz | Villach Süd | 220 | [6 empty] | 2000 |  |  | 2.414 | 27.71 | 362.8999 | 110
Mayrhofen - Zell am Ziller 219 | 14T-220-0-00219R | APG | Mayrhofen | Zell am Ziller | 220 | [6 empty] | 2000 |  |  | 0.25 | 2.8 | 36.9765 | 9.2
Mayrhofen - Zell am Ziller 220 | 14T-220-0-002205 | APG | Mayrhofen | Zell am Ziller | 220 | [6 empty] | 2000 |  |  | 0.25 | 2.8 | 36.9765 | 9.2
Neusiedl - Wien Suedost 246A | 14T-220-0-0246AT | APG | Neusiedl | Wien Suedost | 220 | [6 empty] | 800 |  |  | 3.69 | 18.9 | 126.292 | 45.4
Obersielach - Rosegg 267C | 14T-220-0-0267CE | APG | Obersielach | Rosegg | 220 | [6 empty] | 2000 |  |  | 1.532 | 17.59 | 230.2 | 59.1
Obersielach - Zeltweg 285 | 14T-220-0-00285E | APG | Obersielach | Zeltweg | 220 | [6 empty] | 800 |  |  | 5.841 | 28.73 | 194.78 | 69.3
Oststeiermark - Dreibein Mellach 475SR | 14T-380-0-0475MJ | APG | Oststeiermark | Dreibein Mellach | 400 | [6 empty] | 2400 |  |  | 0.53 | 9.04 | 156.6712 | 28.4
Oststeiermark - Wien Suedost 477 | 14T-380-0-004771 | APG | Oststeiermark | Wien Suedost | 400 | [6 empty] | 2400 |  |  | 2.51 | 42.47 | 735.1326 | 165
St. Peter - Schaerding 235 | 14T-220-0-00235T | APG | St. Peter | Schaerding | 220 | [6 empty] | 800 |  |  | 3.12 | 14.4 | 107.0654 | 36.6
St. Peter - Schaerding 236 | 14T-220-0-00236R | APG | St. Peter | Schaerding | 220 | [6 empty] | 800 |  |  | 3.12 | 14.4 | 107.0654 | 36.6
St. Peter - Salzburg Elixhausen 455 | 14T-220-0-00455F | APG | St. Peter | Salzburg Elixhausen | 400 | [6 empty] | 2400 |  |  | 0.64 | 11.72 | 203.4181 | 45.5
St. Peter - Salzburg Elixhausen 456 | 14T-220-0-00456D | APG | St. Peter | Salzburg Elixhausen | 400 | [6 empty] | 2400 |  |  | 0.64 | 11.72 | 203.4181 | 45.5
Phyrn - Weissenbach 201A | 14T-220-0-0201AN | APG | Phyrn | Weissenbach | 220 | [6 empty] | 925 |  |  | 1.395 | 7.143 | 48.73 | 17.4
Rosegg - Villach Süd 267B | 14T-220-0-0267BG | APG | Rosegg | Villach Süd | 220 | [6 empty] | 2000 |  |  | 0.429 | 4.92 | 64.4 | 59.2
Salzburg Elixhausen - Tauern 231A | 14T-220-0-0231AB | APG | Salzburg Elixhausen | Tauern | 220 | [6 empty] | 800 |  |  | 8.364 | 40.69 | 275.6119 | 98.5
Salzburg Elixhausen - Tauern 232A | 14T-220-0-0232A8 | APG | Salzburg Elixhausen | Tauern | 220 | [6 empty] | 800 |  |  | 8.364 | 40.69 | 275.6119 | 98.5
Sarasdorf - Wien Suedost 435D | 14T-380-0-0435DG | APG | Sarasdorf | Wien Suedost | 400 | [6 empty] | 2300 |  |  | 0.56 | 8.05 | 98.8973 | 26.3
Sarasdorf - Wien Suedost 443D | 14T-380-0-0443DI | APG | Sarasdorf | Wien Suedost | 400 | [6 empty] | 2300 |  |  | 0.56 | 8.05 | 99.18 | 26.3
Sarasdorf - Zurndorf 439A | 14T-380-0-0439AA | APG | Sarasdorf | Zurndorf | 400 | [6 empty] | 2300 |  |  | 0.63 | 8.778 | 108.0079 | 28.7
Sarasdorf - Zurndorf 440A | 14T-380-0-0440AX | APG | Sarasdorf | Zurndorf | 400 | [6 empty] | 2300 |  |  | 0.63 | 8.778 | 108.0079 | 28.7
Schwarzenbach - Tauern 417B | 14T-380-0-0417BM | APG | Schwarzenbach | Tauern | 400 | [6 empty] | 2400 |  |  | 0.142 | 3.742 | 47.5637 | 12.4
Schwarzenbach - Zell am Ziller 417A | 14T-380-0-0417AO | APG | Schwarzenbach | Zell am Ziller | 400 | [6 empty] | 2400 |  |  | 0.651 | 16.93 | 219.4402 | 56.7
Suedburgenland - Dreibein Mellach 476SU | 14T-380-0-0476MG | APG | Suedburgenland | Dreibein Mellach | 400 | [6 empty] | 2400 |  |  | 1.413 | 23.73 | 411.2344 | 61.6
Suedburgenland - Wien Suedost 478 | 14T-381-0-00478Q | APG | Suedburgenland | Wien Suedost | 400 | [6 empty] | 2400 |  |  | 1.633 | 27.76 | 480.3494 | 107.8
Tauern - Zell am Ziller 418 | 14T-380-0-00418H | APG | Tauern | Zell am Ziller | 400 | [6 empty] | 2400 |  |  | 0.79 | 20.67 | 267.0039 | 69.1
Tauern - Weissenbach 221 | 14T-220-0-002213 | APG | Tauern | Weissenbach | 220 | [6 empty] | 800 |  |  | 10.42 | 51.2 | 347.4601 | 123.6
Tauern - Weissenbach 222 | 14T-220-0-002221 | APG | Tauern | Weissenbach | 220 | [6 empty] | 800 |  |  | 10.42 | 51.2 | 347.4601 | 123.6
Ternitz - Wien Suedost 225B | 14T-220-0-0225B1 | APG | Ternitz | Wien Suedost | 220 | [6 empty] | 960 |  |  | 5.075 | 24.59 | 166.065 | 59.5
Ternitz - Wien Suedost 226B | 14T-220-0-0226BZ | APG | Ternitz | Wien Suedost | 220 | [6 empty] | 960 |  |  | 5.075 | 24.59 | 166.065 | 59.5
Wallsee - Ybbsfeld 205B | 14T-220-0-0205B9 | APG | Wallsee | Ybbsfeld | 220 | [6 empty] | 810 |  |  | 2.33 | 12.26 | 83.3465 | 29.7
Westtirol - Zell am Ziller 275 | 14T-220-0-00275H | APG | Westtirol | Zell am Ziller | 220 | [6 empty] | 2100 |  |  | 2.66 | 30.8 | 402.1238 | 103.5
Westtirol - Zell am Ziller 276 | 14T-220-0-00276F | APG | Westtirol | Zell am Ziller | 220 | [6 empty] | 2100 |  |  | 2.66 | 30.8 | 402.1238 | 103.5
Bisamberg - Zaya 443B | 14T-380-0-0443BM | APG | Bisamberg | Zaya | 400 | [6 empty] | 2300 |  |  | 0.904 | 16.34 | 230 | 57.3
Sarasdorf - Zaya 443C | 14T-380-0-443CAE | APG | Sarasdorf | Zaya | 400 | [6 empty] | 2300 |  |  | 1.541 | 25.22 | 342 | 86.6
Vyskov - C. Stred | 27T-TLI-V201---G | CEPS | Vyskov | C. Stred | 220 | [7 empty] | 700 | 900 | 6.62 | 37.14 | 210 | 85
Opocinek - C. Stred | 27T-TLI-V202---B | CEPS | Opocinek | C. Stred | 220 | [7 empty] | 685 | 900 | 6.1 | 28.23 | 177 | 71.3
Opocinek - Sokolnice | 27T-TLI-V203---6 | CEPS | Opocinek | Sokolnice | 220 | [7 empty] | 655 | 900 | 11.73 | 60.17 | 335 | 135.9
Milin - Tabor | 27T-TLI-V204---1 | CEPS | Milin | Tabor | 220 | [7 empty] | 755 | 900 | 3.81 | 25.85 | 150 | 59.3
Malesice - C. Stred | 27T-TLI-V205---X | CEPS | Malesice | C. Stred | 220 | [7 empty] | 755 | 900 | 1.3 | 7.27 | 51 | 19.8
Tabor - Sokolnice | 27T-TLI-V207---N | CEPS | Tabor | Sokolnice | 220 | [7 empty] | 755 | 900 | 10.73 | 72.45 | 426 | 169
Milin - C. Stred | 27T-TLI-V208---I | CEPS | Milin | C. Stred | 220 | [7 empty] | 650 | 900 | 6.92 | 34.3 | 213.3 | 86.2
C. Stred - Bezdecin | 27T-TLI-V209---D | CEPS | C. Stred | Bezdecin | 220 | [6 empty] | 755 |  |  | 4.82 | 28.69 | 190 | 68.4
Bezdecin - Chotejovice | 27T-TLI-V210---F | CEPS | Bezdecin | Chotejovice | 220 | [6 empty] | 656 |  |  | 6.46 | 38.1 | 243 | 97.9
Vyskov - Chotejovice | 27T-TLI-V211---A | CEPS | Vyskov | Chotejovice | 220 | [7 empty] | 755 | 900 | 1.14 | 9.52 | 146 | 30.4
Prestice - Milin | 27T-TLI-V216---M | CEPS | Prestice | Milin | 220 | [7 empty] | 755 | 900 | 4.3 | 27.4 | 180 | 63.8
Prestice - Vitkov | 27T-TLI-V221---4 | CEPS | Prestice | Vitkov | 220 | [6 empty] | 1165 |  |  | 1.77 | 23.9 | 362 | 87.2
Vitkov - Hradec - V223 | 27T-TLI-V223---V | CEPS | Vitkov | Hradec | 220 | [7 empty] | 650 | 900 | 6.23 | 26.85 | 174 | 70
Vitkov - Hradec - V224 | 27T-TLI-V224---Q | CEPS | Vitkov | Hradec | 220 | [7 empty] | 650 | 900 | 6.23 | 26.85 | 174 | 70
Vyskov - Hradec - V225 | 27T-TLI-V225---L | CEPS | Vyskov | Hradec | 220 | [7 empty] | 1000 | 1400 | 2.13 | 9.2 | 103 | 30.7
Vyskov - Hradec - V226 | 27T-TLI-V226---G | CEPS | Vyskov | Hradec | 220 | [7 empty] | 1000 | 1400 | 2.17 | 9.36 | 105 | 31.3
Prosenice - Sokolnice - V251 | 27T-TLI-V251---N | CEPS | Prosenice | Sokolnice | 220 | [7 empty] | 685 | 900 | 6.76 | 35.4 | 220 | 83.9
Prosenice - Sokolnice - V252 | 27T-TLI-V252---I | CEPS | Prosenice | Sokolnice | 220 | [7 empty] | 685 | 900 | 6.76 | 35.4 | 220 | 83.9
Liskovec - Prosenice - V253 | 27T-TLI-V253---D | CEPS | Liskovec | Prosenice | 220 | [7 empty] | 685 | 900 | 5.94 | 27.32 | 178.3 | 71.3
Liskovec - Prosenice - V254 | 27T-TLI-V254---8 | CEPS | Liskovec | Prosenice | 220 | [7 empty] | 685 | 900 | 5.94 | 27.32 | 178.3 | 71.3
C. Stred - Tynec | 27T-TLI-V400---7 | CEPS | C. Stred | Tynec | 400 | [7 empty] | 2100 | 2400 | 1.42 | 14.06 | 180 | 46.2
Tynec - Krasikov | 27T-TLI-V401---2 | CEPS | Tynec | Krasikov | 400 | [6 empty] | 1740 |  |  | 3.12 | 31.62 | 417 | 103.8
Krasikov - Prosenice | 27T-TLI-V402---Y | CEPS | Krasikov | Prosenice | 400 | [6 empty] | 2000 |  |  | 2.34 | 26.61 | 336 | 87.6
Prosenice - Nosovice | 27T-TLI-V403---T | CEPS | Prosenice | Nosovice | 400 | [6 empty] | 1740 |  |  | 2.29 | 23.87 | 280 | 79.6
Kletne - Nosovice | 27T-TLI-V405---J | CEPS | Kletne | Nosovice | 400 | [6 empty] | 1968 |  |  | 1.2 | 14.98 | 210 | 53.5
Vyskov - C. Stred - V410 | 27T-TLI-V410---1 | CEPS | Vyskov | C. Stred | 400 | [6 empty] | 2400 |  |  | 1.97 | 26.3 | 407 | 95.4
Vyskov - Hradec | 27T-TLI-V411---X | CEPS | Vyskov | Hradec | 400 | [7 empty] | 1965 | 2400 | 1.25 | 13.09 | 168 | 45.4
Hradec - Reporyje | 27T-TLI-V412---S | CEPS | Hradec | Reporyje | 400 | [7 empty] | 2010 | 2800 | 3.17 | 35.1 | 513 | 116.9
Reporyje - Mirovka | 27T-TLI-V413RM-R | CEPS | Reporyje | Mirovka | 400 | [7 empty] | 2010 | 2400 | 4.02 | 43.28 | 574 | 145.1
Reporyje - Chodov | 27T-TLI-V414---I | CEPS | Reporyje | Chodov | 400 | [7 empty] | 2265 | 2400 | 0.69 | 8.21 | 113 | 29.5
Chodov - C. Stred | 27T-TLI-V415---D | CEPS | Chodov | C. Stred | 400 | [7 empty] | 2265 | 2400 | 0.82 | 10.5 | 130 | 35.1
Prosenice - Mirovka | 27T-TLI-V416MP-N | CEPS | Prosenice | Mirovka | 400 | [6 empty] | 2000 |  |  | 5.2 | 56.11 | 726 | 184
Otrokovice - Sokolnice | 27T-TLI-V417---3 | CEPS | Otrokovice | Sokolnice | 400 | [6 empty] | 2000 |  |  | 2.21 | 22.43 | 263 | 74.1
Otrokovice - Prosenice | 27T-TLI-V418---Z | CEPS | Otrokovice | Prosenice | 400 | [6 empty] | 2000 |  |  | 1.1 | 11.2 | 134 | 37.7
Vyskov - C. Stred - V419 | 27T-TLI-V419---U | CEPS | Vyskov | C. Stred | 400 | [6 empty] | 2400 |  |  | 1.97 | 26.3 | 407 | 95.4
Hradec - Mirovka | 27T-TLI-V420---W | CEPS | Hradec | Mirovka | 400 | [7 empty] | 2010 | 2400 | 5.9 | 60.38 | 767 | 209.6
Cebin - Mirovka | 27T-TLI-V422---M | CEPS | Cebin | Mirovka | 400 | [7 empty] | 2055 | 2400 | 2.34 | 26.61 | 337 | 88.4
Cebin - Sokolnice | 27T-TLI-V423---H | CEPS | Cebin | Sokolnice | 400 | [6 empty] | 2000 |  |  | 1.04 | 11.44 | 154 | 38.3
Hradec - Chrast | 27T-TLI-V430---Q | CEPS | Hradec | Chrast | 400 | [7 empty] | 2235 | 2400 | 2.02 | 24.85 | 318 | 82.2
Chrast - Prestice | 27T-TLI-V431---L | CEPS | Chrast | Prestice | 400 | [7 empty] | 2235 | 2400 | 0.8 | 9.46 | 122 | 32.6
Prestice - Kocin | 27T-TLI-V432---G | CEPS | Prestice | Kocin | 400 | [7 empty] | 2235 | 2400 | 2.64 | 33.01 | 426 | 115.9
Dasny - Slavetice | 27T-TLI-V433---B | CEPS | Dasny | Slavetice | 400 | [7 empty] | 2235 | 2800 | 3.46 | 42.53 | 575 | 142.7
Cebin - Slavetice | 27T-TLI-V434---6 | CEPS | Cebin | Slavetice | 400 | [6 empty] | 1968 |  |  | 1.09 | 13.92 | 194 | 50.7
Slavetice - Sokolnice - V435 | 27T-TLI-V435---1 | CEPS | Slavetice | Sokolnice | 400 | [6 empty] | 2000 |  |  | 1.33 | 15.33 | 238 | 55.6
Slavetice - Sokolnice - V436 | 27T-TLI-V436---X | CEPS | Slavetice | Sokolnice | 400 | [6 empty] | 2000 |  |  | 1.34 | 15.54 | 236 | 55.6
Vyskov - Babylon | 27T-TLI-V450---E | CEPS | Vyskov | Babylon | 400 | [7 empty] | 2235 | 2400 | 1.66 | 21.46 | 287 | 72.3
Bezdecin - Babylon | 27T-TLI-V451---9 | CEPS | Bezdecin | Babylon | 400 | [7 empty] | 2235 | 2400 | 1.28 | 16.02 | 217 | 53.6
Bezdecin - Neznasov | 27T-TLI-V452---4 | CEPS | Bezdecin | Neznasov | 400 | [7 empty] | 2265 | 2400 | 1.58 | 20.53 | 260 | 68.3
Neznasov - Krasikov | 27T-TLI-V453--X5 | CEPS | Neznasov | Krasikov | 400 | [6 empty] | 2000 |  |  | 2.4 | 25.3 | 297 | 84.1
C. Stred - Bezdecin | 27T-TLI-V454---V | CEPS | C. Stred | Bezdecin | 400 | [7 empty] | 2265 | 2400 | 1.55 | 18.24 | 291 | 67.6
H. Zivotice - Krasikov | 27T-TLI-V458---B | CEPS | H. Zivotice | Krasikov | 400 | [6 empty] | 2000 |  |  | 2.51 | 31.34 | 429 | 107
H. Zivotice - Kletne | 27T-TLI-V459---6 | CEPS | H.Zivotice | Kletne | 400 | [6 empty] | 1968 |  |  | 0.98 | 11.79 | 166 | 42.1
Nosovice - Albrechtice | 27T-TLI-V460---8 | CEPS | Nosovice | Albrechtice | 400 | [6 empty] | 2000 |  |  | 0.48 | 5.01 | 58 | 16.5
Kocin - Dasny - V473 | 27T-TLI-V473---O | CEPS | Kocin | Dasny | 400 | [7 empty] | 2235 | 2400 | 0.83 | 10 | 141 | 35.6
Kocin - Dasny - V474 | 27T-TLI-V474---J | CEPS | Kocin | Dasny | 400 | [7 empty] | 2295 | 2400 | 0.98 | 11.87 | 187 | 42.9
Reporyje - Kocin | 27T-TLI-V475---E | CEPS | Reporyje | Kocin | 400 | [6 empty] | 2265 |  |  | 2.91 | 37.28 | 599 | 137.7
Kocin - Chodov | 27T-TLI-V476---9 | CEPS | Kocin | Chodov | 400 | [6 empty] | 2265 |  |  | 2.91 | 36.14 | 505 | 129
Chotejovice - Vyskov | 27T-TLI-V480---X | CEPS | Chotejovice | Vyskov | 400 | [6 empty] | 2000 |  |  | 0.69 | 8.03 | 122 | 28.9
Vitkov - Prestice | 27T-TLI-V490---R | CEPS | Vitkov | Prestice | 400 | [6 empty] | 1600 |  |  | 1.76 | 23.9 | 360 | 86.8
Roost - Flebour Ost | - | Creos | ROOST | FLEBOUR | 220 | [6 empty] | 1290 |  |  | 1.022 | 5.144 | 44.2745 | 17.6 | none
Roost - Flebour West | - | Creos | ROOST | FLEBOUR | 220 | [6 empty] | 1290 |  |  | 1.022 | 5.144 | 44.2745 | 17.6 | none
Heisdorf - Blooren | - | Creos | BLOOREN | HEISDORF | 220 | [6 empty] | 1290 |  |  | 0.676 | 3.611 | 261.6947 | 13.5 | none
Heisdorf - Roost Ost | - | Creos | HEISDORF | ROOST | 220 | [6 empty] | 1290 |  |  | 0.779 | 3.923 | 33.615 | 13.4 | none
Heisdorf - Roost West | - | Creos | HEISDORF | ROOST | 220 | [6 empty] | 1290 |  |  | 0.779 | 3.963 | 33.615 | 13.4 | none
Heisdorf - Bertrange Ost | - | Creos | HEISDORF | BERTRANGE | 220 | [6 empty] | 1290 |  |  | 0.645 | 3.28 | 27.9602 | 11.1 | none
Heisdorf - Bertrange West | - | Creos | HEISDORF | BERTRANGE | 220 | [6 empty] | 1290 |  |  | 0.645 | 3.28 | 27.9602 | 11.1 | none
Schifflange - Berchem | - | Creos | SCHIFFLANGE | BERCHEM | 220 | [6 empty] | 1290 |  |  | 1.0117 | 3.9274 | 248.2644 | 12.9 | none
Schifflange - Sotel - Oxylux | - | Creos | OXYLUX | SCHIFFLANGE | 220 | [6 empty] | 1290 |  |  | 0.282 | 1.66 | 179.3849 | 8.7 | none
Schifflange - Oxylux | - | Creos | SCHIFFLANGE | OXYLUX | 220 | [6 empty] | 1290 |  |  | 0.376 | 2.164 | 204.2035 | 8.2 | none
Bertrange - Schifflange Ost | - | Creos | SCHIFFLANGE | BERTRANGE | 220 | [6 empty] | 1290 |  |  | 0.604 | 3.072 | 26.0752 | 10.4 | none
Bertrange - Schifflange West | - | Creos | BERTRANGE | SCHIFFLANGE | 220 | [6 empty] | 1290 |  |  | 0.604 | 3.072 | 26.0752 | 10.4 | none
Blooren - Berchem | - | Creos | BLOOREN | BERCHEM | 220 | [6 empty] | 1290 |  |  | 0.36 | 1.986 | 222.7389 | 8.6 | none
Blooren - Schifflange | - | Creos | SCHIFFLANGE | BLOOREN | 220 | [6 empty] | 1290 |  |  | 1.156 | 6.037 | 256.9823 | 21.6 | none
Heisdorf Quint Nord | 10T-LU-DE-00003C | Creos | HEISDORF | QUINT | 220 | [6 empty] | 1290 |  |  | 2.9235 | 14.604 | 126.5434 | 50.3 | none
Blooren Trier Süd | 10T-LU-DE-00002E | Creos | BLOOREN | TRIER | 220 | [6 empty] | 1290 |  |  | 2.737 | 14.143 | 402.1239 | 49.5 | none
Flebour Bauler Nord | 10T-LU-DE-00001G | Creos | FLEBOUR | BAULER | 220 | [6 empty] | 2500 |  |  | 0.386 | 2.572 | 32.9867 | 10.3 | DLR (Ampacimon) removed , lines replaced by HTLS cables
Flebour Bauler Süd | 10T1001C--00096F | Creos | FLEBOUR | BAULER | 220 | [6 empty] | 1290 |  |  | 0.2975 | 1.498 | 12.893 | 10.3 | DLR (Ampacimon) removed , lines replaced by HTLS cables
Schifflange PST-Schifflange | 10T-BE-LU-000011 | Creos | SCHIFFLANGE | AUBANGE | 220 | [6 empty] | 982 |  |  | 0.0029 | 0.05 | 0.19164 | 0.1
Podlog - Cirkovce | 28T000000000301K | ELES | Podlog | Cirkovce | 400 | [6 empty] | 1920 |  |  | 1.5912 | 17.116 | 18.9629 | 53.47
Bericevo - Krsko | 28T-0000000209-C | ELES | Bericevo | Krsko | 400 | [6 empty] | 1920 |  |  | 2.15 | 22.95 | 245.8999 | 80.4
Bericevo - Krsko | 28T-0000000210-Z | ELES | Bericevo | Krsko | 400 | [6 empty] | 1920 |  |  | 2.15 | 22.95 | 245.8999 | 80.4
Bericevo - Klece | 28T-0000000195-U | ELES | Bericevo | Klece | 220 | [6 empty] | 960 |  |  | 0.78 | 5.27 | 38.0001 | 13.19
Bericevo - Podlog | 28T-0000000208-F | ELES | Bericevo | Podlog | 400 | [6 empty] | 1920 |  |  | 1.53 | 16.35 | 177.4999 | 50.1
Okroglo - Bericevo | 28T-0000000206-L | ELES | Okroglo | Bericevo | 400 | [6 empty] | 1600 |  |  | 0.93 | 9.89 | 152.9 | 31.38
Okroglo - Bericevo | 28T-0000000207-I | ELES | Okroglo | Bericevo | 400 | [6 empty] | 1600 |  |  | 0.93 | 9.89 | 152.9 | 31.38
Divaca - Klece | 28T-0000000200-2 | ELES | Divaca | Klece | 220 | [6 empty] | 960 |  |  | 3.93 | 27.31 | 185.9998 | 66.32
Podlog - Sostanj | 28T-0000000215-K | ELES | Podlog | Sostanj | 400 | [6 empty] | 1680 |  |  | 0.4017 | 4.2249 | 45.8801 | 12.96
Cirkovce - Krsko | 28T000000000300M | ELES | Cirkovce | Krsko | 400 | [6 empty] | 1920 |  |  | 1.7669 | 18.454 | 205.259 | 57.83
Podlog - Bericevo | 28T-0000000196-R | ELES | Podlog | Bericevo | 220 | [6 empty] | 960 |  |  | 3.74 | 25.86 | 178.1 | 63.18
Divaca - Bericevo | 28T-0000000205-O | ELES | Divaca | Bericevo | 400 | [6 empty] | 1920 |  |  | 2.33 | 24.86 | 269.8998 | 76.17
Maribor - Cirkovce | 28T000000000303G | ELES | Maribor | Cirkovce | 400 | [6 empty] | 1920 |  |  | 0.5667 | 5.9192 | 65.8349 | 18.41
Maribor - Cirkovce | 28T000000000302I | ELES | Maribor | Cirkovce | 400 | [6 empty] | 1920 |  |  | 0.5667 | 5.9192 | 65.8349 | 18.41
Podlog - Cirkovce | 28T-0000000196-R | ELES | Podlog | Cirkovce | 220 | [6 empty] | 960 |  |  | 3.01 | 20.98 | 142.3 | 50.92
Divaca - Divaca |  | ELES | Divaca | Divaca | 400 | [6 empty] | 2880 |  |  | 0 | 0 | 0 |  | Coupler
Podlog - Podlog |  | ELES | Podlog | Podlog | 220 | [6 empty] | 960 |  |  | 0 | 0 | 0 |  | Coupler
Cirkovce - Cirkovce |  | ELES | Cirkovce | Cirkovce | 400 | [6 empty] | 1920 |  |  | 0 | 0 | 0 |  | Coupler
Bericevo - Bericevo |  | ELES | Bericevo | Bericevo | 400 | [6 empty] | 1920 |  |  | 0 | 0 | 0 |  | Coupler
Krsko - Krsko |  | ELES | Krsko | Krsko | 400 | [6 empty] | 2880 |  |  | 0 | 0 | 0 |  | Coupler
Maribor - Maribor |  | ELES | Maribor | Maribor | 400 | [6 empty] | 1920 |  |  | 0 | 0 | 0 |  | Coupler
Divaca - Divaca |  | ELES | Divaca | Divaca | 220 | [6 empty] | 960 |  |  | 0 | 0 | 0 |  | Coupler
Sostanj - Sostanj |  | ELES | Sostanj | Sostanj | 400 | [6 empty] | 9999 |  |  | 0 | 0 | 0 |  | Coupler
AUBANGE – BRUME 380.13 | 22T-BE-IN-LI0211 | ELIA | AUBANGE | BRUME | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 3.5493 | 32.8832 | 379.3569 | 104.391
DOEL – ZANDVLIET 380.25 | 22T-BE-IN-LI02AK | ELIA | DOEL | ZANDVLIET | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  | 1999 | 2350.824 | 0.24259 | 2.3999 | 24 | 6.8
DOEL – MERCATOR 380.54 | 22T-BE-IN-LI016V | ELIA | DOEL | MERCATOR | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.79853 | 6.8373 | 80 | 22.2
LINT – MASSENHOVEN 380.61 | 22T-BE-IN-LI009S | ELIA | LINT | MASSENHOVEN | 400 | 2450.56 | 2319.28 | 2188 | 2319.28 | 2450.56 |  |  |  |  | 0.46064 | 4.5602 | 50.1676 | 14.06
MASSENHOVEN – MEERHOUT 380.21 | 22T-BE-IN-LI0041 | ELIA | MASSENHOVEN | MEERHOUT | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 1.0079 | 10.6596 | 125.4003 | 32.5
MASSENHOVEN – MERCATOR 380.60 | 22T-BE-IN-LI0106 | ELIA | MASSENHOVEN | MERCATOR | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 1.0917 | 11.5448 | 123.1994 | 35
LINT – MERCATOR 380.59 | 22T20180112---7F | ELIA | LINT | MERCATOR | 400 | 2448.6941 | 2317.514 | 2186.334 | 2317.514 | 2448.6941 |  |  |  |  | 0.65413 | 6.9196 | 73.8006 | 21.1
LINT – MERCATOR 380.61 | 22T-BE-IN-LI009S | ELIA | LINT | MERCATOR | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.65413 | 6.9196 | 73.8006 | 21.1
MEERHOUT – VAN EYCK 380.23 | 22T-BE-IN-LI017T | ELIA | MEERHOUT | VAN EYCK | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 1.7819 | 18.86 | 220.8615 | 57.5 | Wrong conductor data in previous SGM, now updated
MEERHOUT – VAN EYCK 380.24 | 22T20220113----0 | ELIA | MEERHOUT | VAN EYCK | 400 | [6 empty] | 3814 |  |  | 2.1808 | 18.709 | 201.7832 | 57.39 | New element compared to previous SGM
Y – MERCATOR (– BRUEGHEL – VERBRANDE BRUG) 380.36 | 22T-BE-IN-LI006Y | ELIA | AFTAKKING BUGGENHOUT 380kV | MERCATOR | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.47941 | 5.0843 | 58.8006 | 15.5
Y – MERCATOR (– BRUEGHEL – VERBRANDE BRUG) 380.35 | 22T-BE-IN-LI0-52 | ELIA | AFTAKKING BUGGENHOUT 380kV | MERCATOR | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  | 1999 | 2350.824 | 0.5906 | 5.0006 | 58.5997 | 15.5 | Use of Ampacimon allowing for DLR compared to previous SGM
Y – MERCATOR (– HORTA – RODENHUIZE) 380.74 | 22T20161020---3A | ELIA | MERCATOR | AFTAKKING RODENHUIZE 380kV | 400 | 4399.92 | 4259.808 | 4139.856 | 4259.808 | 4399.92 |  |  |  |  | 0.61506 | 10.9344 | 121.7135 | 34.17
Y – VERBRANDE BRUG (– BRUEGHEL – MERCATOR) 380.36 | 22T-BE-IN-LI006Y | ELIA | AFTAKKING BUGGENHOUT 380kV | VERBRANDE BRUG | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.6729 | 7.1175 | 83.4585 | 21.7
Y – VERBRANDE BRUG (– BRUEGHEL – MERCATOR) 380.35 | 22T-BE-IN-LI0-52 | ELIA | AFTAKKING BUGGENHOUT 380kV | VERBRANDE BRUG | 400 | 2597.28 | 2458.14 | 2319 | 2458.14 | 2597.28 |  |  | 1999 | 2350.824 | 0.65846 | 6.9095 | 83.4585 | 21.7 | Use of Ampacimon allowing for DLR compared to previous SGM
CHAMPION (NAMUR) – COURCELLES 380.56 | 22T-BE-IN-LI0033 | ELIA | CHAMPION (NAMUR) | COURCELLES | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 1.3675 | 14.4645 | 170.2438 | 44.1
BRUEGEL – COURCELLES 380.34 | 22T-BE-IN-LI0025 | ELIA | BRUEGEL | COURCELLES | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 1.4657 | 15.5143 | 182.5997 | 47.3
COURCELLES – GOUY 380.58 | 22T20180112---5J | ELIA | COURCELLES | GOUY | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.060648 | 0.5906 | 7 | 1.8
COURCELLES – GOUY 380.57 | 22T20180112---4L | ELIA | COURCELLES | GOUY | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  |  |  | 0.05054 | 0.56027 | 6.5997 | 1.7
Y – COURCELLES (– BRUEGHEL – DROGENBOS) 380.33 | 22T-BE-IN-LI0017 | ELIA | COURCELLES | AFTAKKING MEKINGEN 380kV | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  |  |  | 1.0296 | 10.9498 | 128.1994 | 33.4
Y – BRUEGHEL (– MERCATOR – VERBRANDE BRUG) 380.36 | 22T-BE-IN-LI006Y | ELIA | BRUEGEL | AFTAKKING BUGGENHOUT 380kV | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.49962 | 5.2504 | 61.8006 | 15.9
Y – BRUEGHEL (– MERCATOR – VERBRANDE BRUG) 380.35 | 22T-BE-IN-LI0-52 | ELIA | BRUEGEL | AFTAKKING BUGGENHOUT 380kV | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  | 1999 | 2350.824 | 0.60937 | 5.1103 | 59.8006 | 15.9 | Use of Ampacimon allowing for DLR compared to previous SGM
Y – BRUEGHEL (– COURCELLES – DROGENBOS) 380.33 | 22T-BE-IN-LI0017 | ELIA | BRUEGEL | AFTAKKING MEKINGEN 380kV | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  |  |  | 0.45053 | 4.6251 | 54.1801 | 14
EEKLO NOORD – HORTA 380.103 | 22T20180102---3U | ELIA | EEKLO NOORD | HORTA | 400 | 5107.2 | 4833.6 | 4560 | 4833.6 | 5107.2 |  |  |  |  | 0.4036 | 4.2644 | 50.267 | 13
AVELGEM – HORTA 380.101 | 22T20161020----I | ELIA | AVELGEM | HORTA | 400 | 4460 | 4340 | 4232 | 4340 | 4460 |  |  |  |  | 0.6749 | 12.1879 | 147.3664 | 39.7
AVELGEM – IZEGEM 380.46 | 22T-BE-IN-LI043S | ELIA | AVELGEM | IZEGEM | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.70612 | 7.4756 | 87.6496 | 22.8
AVELGEM – IZEGEM 380.47 | 22T-BE-IN-LI042U | ELIA | AVELGEM | IZEGEM | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.70612 | 7.4756 | 87.6496 | 22.8
Y – RODENHUIZE (– HORTA – MERCATOR) 380.74 | 22T20161020---3A | ELIA | AFTAKKING RODENHUIZE 380kV | RODENHUIZE | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.01444 | 0.1444 | 0 | 0.2
Y – DROGENBOS (– BRUEGHEL – COURCELLES) 380.33 | 22T-BE-IN-LI0017 | ELIA | DROGENBOS | AFTAKKING MEKINGEN 380kV | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.31912 | 3.3804 | 39.6136 | 10.3
BRUME – CENTRALE COO 380.3 | 22T20180112---2P | ELIA | BRUME | CENTRALE COO | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  |  |  | 0.062092 | 0.65558 | 7.7202 | 2
BRUME – CENTRALE COO 380.4 | 22T20180112---3N | ELIA | BRUME | CENTRALE COO | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  |  |  | 0.062092 | 0.65558 | 7.7202 | 2
GRAMME – TIHANGE 1 380.5 | 22T201908261---Z | ELIA | GRAMME | TIHANGE 1 | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  |  |  | 0.089528 | 0.9516 | 11.1939 | 2.9
GRAMME – TIHANGE 1 380.6 | 22T201908262---U | ELIA | GRAMME | TIHANGE 1 | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  |  |  | 0.089528 | 0.9516 | 11.1939 | 2.9
GRAMME – TIHANGE 2 380.17 | 22T20180112---6H | ELIA | GRAMME | TIHANGE 2 | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.080864 | 0.8534 | 10.0402 | 2.6
TIHANGE BIS – TIHANGE 2 380.15 | 22T20180112---8D | ELIA | TIHANGE BIS | TIHANGE 2 | 400 | 2600.64 | 2461.32 | 2322 | 2461.32 | 2600.64 |  |  |  |  | 0.030324 | 0.31335 | 3.8006 | 1
GRAMME – TIHANGE 3 380.18 | 22T201908263---P | ELIA | GRAMME | TIHANGE 3 | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.10252 | 1.0816 | 12.7396 | 3.3
BRUME – GRAMME 380.1 | 22T-BE-IN-LI007W | ELIA | BRUME | GRAMME | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  |  |  | 1.3732 | 14.5295 | 164 | 44.3
BRUME – GRAMME 380.2 | 22T-BE-IN-LI008U | ELIA | BRUME | GRAMME | 400 | 2600.64 | 2461.32 | 2322 | 2461.32 | 2600.64 |  |  |  |  | 1.3732 | 14.5295 | 170.3795 | 44.3
CHAMPION (NAMUR) – GRAMME 380.32 | 22T-BE-IN-LI0203 | ELIA | CHAMPION (NAMUR) | GRAMME | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  | 2186 | 2570.736 | 0.99925 | 10.5614 | 124.2465 | 32.2
ACHENE – GRAMME 380.10 | 22T-BE-IN-LI0130 | ELIA | ACHENE | GRAMME | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  | 1999 | 2350.824 | 1.1436 | 12.1036 | 141.4737 | 36.9
GRAMME – RIMIERE 380.7 | 22T-BE-IN-LI044Q | ELIA | GRAMME | RIMIERE | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  |  |  | 0.45342 | 4.7883 | 54 | 14.6
ACHENE – ACHENE SNCB 380.200 | 22T20211201A---V | ELIA | ACHENE | ACHENE SNCB | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.01444 | 0.1444 | 0 | 0.05
DOEL – ZANDVLIET 380.26 | 22T20170512----9 | ELIA | DOEL | ZANDVLIET | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  | 1999 | 2350.824 | 0.07074 | 2.5749 | 22.9198 | 7.074
Y – GRAMME (– ANDRE DUMONT – VAN EYCK) 380.12 | 22T20161020---48 | ELIA | GRAMME | AFTAKKING ZUTTENDAAL 380kV | 400 | 2240 | 2120 | 2000 | 2120 | 2240 |  |  |  |  | 1.8459 | 17.4528 | 202.6954 | 55.6
Y – ANDRE DUMONT (– GRAMME – VAN EYCK) 380.12 | 22T20161020---48 | ELIA | ANDRE DUMONT | AFTAKKING ZUTTENDAAL 380kV | 400 | 2240 | 2120 | 2000 | 2120 | 2240 |  |  |  |  | 0.20916 | 1.9776 | 22.9673 | 6.3
AVELGEM – HORTA 380.102 | 22T20161020---1E | ELIA | AVELGEM | HORTA | 400 | 4460 | 4340 | 4232 | 4340 | 4460 |  |  |  |  | 0.71325 | 12.1649 | 147.088 | 39.625
Y – HORTA (– MERCATOR – RODENHUIZE) 380.74 | 22T20161020---3A | ELIA | HORTA | AFTAKKING RODENHUIZE 380kV | 400 | 5316.192 | 5173.056 | 5040 | 5173.056 | 5316.192 |  |  |  |  | 0.25556 | 4.5434 | 50.5733 | 14.198
Y – VAN EYCK (– ANDRE DUMONT – GRAMME) 380.12 | 22T20161020---48 | ELIA | VAN EYCK | AFTAKKING ZUTTENDAAL 380kV | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  |  |  | 0.7153 | 9.5477 | 114.3547 | 31.1
EEKLO NOORD – MAERLANT 380.103 | 22T20180102---3U | ELIA | EEKLO NOORD | MAERLANT | 400 | 5251.68 | 4970.34 | 4689 | 4970.34 | 5251.68 |  |  |  |  | 0.2768 | 4.0655 | 79.5973 | 17.3
HORTA – MAERLANT 380.104 | 22T20180104----Q | ELIA | HORTA | MAERLANT | 400 | 5251.68 | 4970.34 | 4689 | 4970.34 | 5251.68 |  |  |  |  | 0.43448 | 7.9364 | 115.831 | 28.965
GEZELLE – MAERLANT 380.107 | 22T20180104---2K | ELIA | GEZELLE | MAERLANT | 400 | 1635 | 1635 | 1635 | 1635 | 1635 |  |  | 1635 | 1716.75 | 0.09045 | 2.2412 | 725.811 | 10.05
GEZELLE – MAERLANT 380.108 | 22T20180104---3I | ELIA | GEZELLE | MAERLANT | 400 | 1635 | 1635 | 1635 | 1635 | 1635 |  |  | 1635 | 1716.75 | 0.09045 | 2.2311 | 725.811 | 10.05
GEZELLE – MAERLANT 380.109 | 22T20180104---4G | ELIA | GEZELLE | MAERLANT | 400 | 1635 | 1635 | 1635 | 1635 | 1635 |  |  | 1635 | 1716.75 | 0.11055 | 2.211 | 725.811 | 10.05
GEZELLE – MAERLANT 380.110 | 22T20180104---5E | ELIA | GEZELLE | MAERLANT | 400 | 1635 | 1635 | 1635 | 1635 | 1635 |  |  | 1635 | 1716.75 | 0.11055 | 2.211 | 725.811 | 10.05
GEZELLE – STEVIN 380.111 | 22T20180104---6C | ELIA | GEZELLE | STEVIN | 400 | 5201.28 | 4922.64 | 4644 | 4922.64 | 5201.28 |  |  |  |  | 0.132 | 1.8952 | 18.4192 | 8
GEZELLE – STEVIN 380.112 | 22T20180104---7A | ELIA | GEZELLE | STEVIN | 400 | 5201.28 | 4922.64 | 4644 | 4922.64 | 5201.28 |  |  |  |  | 0.132 | 1.8952 | 18.4192 | 8
GRAMME – LIXHE 380.11 | 22T-BE-IN-LI018R | ELIA | GRAMME | LIXHE | 400 | 2297.2466 | 2174.1798 | 2051.113 | 2174.1798 | 2297.2466 |  |  | 2051.113 | 2412.1089 | 3.0438 | 20.025 | 170.88 | 53.4
LIXHE – VAN EYCK 380.91 | 22T20180102---2W | ELIA | LIXHE | VAN EYCK | 400 | 2240 | 2120 | 2000 | 2120 | 2240 |  |  | 2000 | 2352 | 2.0695 | 16.5259 | 192.9604 | 53
ALEGRO CONVERTOR STATION – LIXHE 380.115 | 22T20200610----Z | ELIA | ALEGRO CONVERTOR STATION | LIXHE | 400 | 1591 | 1591 | 1591 | 1591 | 1591 |  |  |  |  | 0.0033165 | 0.034505 | 24.5341 | 0.335
Y – COURCELLES (– GRAMME – SAINT-AMAND) 380.31 | 22T-BE-IN-LI019P | ELIA | COURCELLES | REPIQUAGE ST-AMAND 380kV | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  | 1999 | 2350.824 | 0.38988 | 4.1313 | 48.6357 | 12.6
Y – GRAMME (– COURCELLES – SAINT-AMAND) 380.31 | 22T-BE-IN-LI019P | ELIA | GRAMME | REPIQUAGE ST-AMAND 380kV | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  | 1999 | 2350.824 | 1.7472 | 18.4991 | 217.8006 | 56.4
Y – SAINT-AMAND (– COURCELLES – GRAMME) 380.31 | 22T-BE-IN-LI019P | ELIA | REPIQUAGE ST-AMAND 380kV | TERGNEE | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  | 2186 | 2570.736 | 0.23248 | 2.4606 | 27.7604 | 7.5
LILLO – ZANDVLIET 380.65 | 22T20191001D---0 | ELIA | LILLO | ZANDVLIET | 400 | 3340 | 3077 | 2816 | 3077 | 3340 |  |  |  |  | 0.30677 | 5.2492 | 65.411 | 17.043
Y – DOEL (– LILLO – MERCATOR) 380.51 | 22T-BE-IN-LI014Z | ELIA | DOEL | AFTAKKING LIEFKENSHOEK 380kV | 400 | 2240 | 2120 | 2000 | 2120 | 2240 |  |  |  |  | 0.16442 | 1.7185 | 20.1976 | 5.304
Y – LILLO (– DOEL – MERCATOR) 380.51 | 22T-BE-IN-LI014Z | ELIA | AFTAKKING LIEFKENSHOEK 380kV | LILLO | 400 | 3248 | 3074 | 2900 | 3074 | 3248 |  |  |  |  | 0.08862 | 0.9419 | 8.0568 | 2.532
Y – MERCATOR (– DOEL – LILLO) 380.51 | 22T-BE-IN-LI014Z | ELIA | AFTAKKING LIEFKENSHOEK 380kV | MERCATOR | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  |  |  | 0.52757 | 5.5761 | 65.614 | 17
Y – DOEL (– LILLO – KALLO) 380.52 | 22T-BE-IN-LI015X | ELIA | DOEL | AFTAKKING LIEFKENSHOEK 380kV | 400 | 2240 | 2120 | 2000 | 2120 | 2240 |  |  |  |  | 0.16433 | 1.7228 | 20.1968 | 5.301
Y – LILLO (– DOEL – KALLO) 380.52 | 22T-BE-IN-LI015X | ELIA | AFTAKKING LIEFKENSHOEK 380kV | LILLO | 400 | 3248 | 3074 | 2900 | 3074 | 3248 |  |  |  |  | 0.087156 | 0.92966 | 7.9699 | 2.421
LILLO – ZANDVLIET 380.66 | 22T20191001C---5 | ELIA | LILLO | ZANDVLIET | 400 | 2525 | 2375 | 2216 | 2375 | 2525 |  |  |  |  | 0.28368 | 4.8541 | 60.4869 | 15.76
DOEL – MERCATOR 380.53 | 22T20180102----1 | ELIA | DOEL | MERCATOR | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.79853 | 6.8373 | 80 | 22.2
Y – HORTA (– MERCATOR – RODENHUIZE) 380.73 | 22T20161020---2C | ELIA | HORTA | AFTAKKING RODENHUIZE 380kV | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.22717 | 4.5008 | 51.1696 | 14.198
Y – MERCATOR (– HORTA – RODENHUIZE) 380.73 | 22T20161020---2C | ELIA | MERCATOR | AFTAKKING RODENHUIZE 380kV | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.54672 | 10.8319 | 123.1487 | 34.17
Y – RODENHUIZE (– HORTA – MERCATOR) 380.73 | 22T20161020---2C | ELIA | AFTAKKING RODENHUIZE 380kV | RODENHUIZE | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  |  |  | 0.0032 | 0.0634 | 0.7208 | 0.2
Y – KALLO (– DOEL – LILLO) 380.52 | 22T-BE-IN-LI015X | ELIA | KALLO | AFTAKKING LIEFKENSHOEK 380kV | 400 | 2240 | 2120 | 2000 | 2120 | 2240 |  |  |  |  | 0.1302 | 1.365 | 16.002 | 4.2
KALLO – MERCATOR 380.52 | 22T-BE-IN-LI015X | ELIA | KALLO | MERCATOR | 400 | 2240 | 2120 | 2000 | 2120 | 2240 |  |  |  |  | 0.4123 | 4.3225 | 50.673 | 13.3
LA TROQUE – SERAING 220.524 | 22T20211201C---L | ELIA | LA TROQUE | SERAING | 220 | 1176 | 1113 | 1050 | 1113 | 1176 |  |  |  |  | 0.1452 | 1.0125 | 7.0331 | 2.5
LA TROQUE – SERAING 220.525 | 22T20211201D---G | ELIA | LA TROQUE | SERAING | 220 | 1176 | 1113 | 1050 | 1113 | 1176 |  |  |  |  | 0.1452 | 1.0125 | 7.0331 | 2.5
BERNEAU – POSTE DE TRANSITION LONGUE VUE 220kV 220.531 | 22T-BE-IN-LI024W | ELIA | BERNEAU | POSTE DE TRANSITION LONGUE VUE 220kV | 220 | 1365 | 1365 | 1365 | 1365 | 1365 |  |  |  |  | 0.6052 | 3.1773 | 132.4676 | 8.9 | THE NODE "POSTE DE TRANSITION LONGUE VUE 220kV" IS A LINE-CABLE TRANSITION, MEANING THAT BOTH ENDS OF THE LINE 220.531 CAN BE CONNECTED IN SERIES
POSTE DE TRANSITION LONGUE VUE 220kV – JUPILLE 220.531 | 22T-BE-IN-LI024W | ELIA | POSTE DE TRANSITION LONGUE VUE 220kV | JUPILLE | 220 | 995.68 | 942.34 | 889 | 942.34 | 995.68 |  |  |  |  | 0.6052 | 3.1773 | 132.4676 | 8.9 | THE NODE "POSTE DE TRANSITION LONGUE VUE 220kV" IS A LINE-CABLE TRANSITION, MEANING THAT BOTH ENDS OF THE LINE 220.531 CAN BE CONNECTED IN SERIES
RIMIERE – SERAING 220.533 | 22T-BE-IN-LI032X | ELIA | RIMIERE | SERAING | 220 | 1161.44 | 1099.22 | 1037 | 1099.22 | 1161.44 |  |  |  |  | 0.66018 | 4.6299 | 31.8016 | 11.4
BERNEAU – POSTE DE TRANSITION LONGUE VUE 220kV 220.541 | 22T-BE-IN-LI023Y | ELIA | BERNEAU | POSTE DE TRANSITION LONGUE VUE 220kV | 220 | 1365 | 1365 | 1365 | 1365 | 1365 |  |  |  |  | 0.1625 | 0.91 | 120.952 | 3.25 | THE NODE "POSTE DE TRANSITION LONGUE VUE 220kV" IS A LINE-CABLE TRANSITION, MEANING THAT BOTH ENDS OF THE LINE 220.541 CAN BE CONNECTED IN SERIES
POSTE DE TRANSITION LONGUE VUE 220kV – LIXHE 220.541 | 22T-BE-IN-LI023Y | ELIA | POSTE DE TRANSITION LONGUE VUE 220kV | LIXHE | 220 | 995.68 | 942.34 | 889 | 942.34 | 995.68 |  |  |  |  | 0.1625 | 0.91 | 120.952 | 3.25 | THE NODE "POSTE DE TRANSITION LONGUE VUE 220kV" IS A LINE-CABLE TRANSITION, MEANING THAT BOTH ENDS OF THE LINE 220.541 CAN BE CONNECTED IN SERIES
Q1 – BASTOGNE (– MARCOURT – RIMIERE – SENONCHAMPS – VILLEROUX) 220.501 | 22T-BE-IN-LI033V | ELIA | BASTOGNE | REPIQUAGE SENONCHAMPS 220kV | 220 | 1190.56 | 1126.78 | 1063 | 1126.78 | 1190.56 |  |  |  |  | 0.1302 | 0.45012 | 4.9008 | 1.5
HEINSCH – VILLEROUX 220.505 | 22T-BE-IN-LI036P | ELIA | HEINSCH | VILLEROUX | 220 | 1190.56 | 1126.78 | 1063 | 1126.78 | 1190.56 |  |  |  |  | 3.433 | 9.6698 | 108.4215 | 33.2
AUBANGE – HEINSCH 220.507 | 22T-BE-IN-LI037N | ELIA | AUBANGE | HEINSCH | 220 | 1190.56 | 1126.78 | 1063 | 1126.78 | 1190.56 |  |  |  |  | 1.603 | 4.4102 | 48.9793 | 15
Y – BRUME (– HOUFFALIZE – VILLEROUX) 220.504 | 22T-BE-IN-LI034T | ELIA | BRUME | REPIQUAGE HOUFFALIZE 220kV | 220 | 1393.28 | 1318.64 | 1244 | 1318.64 | 1393.28 |  |  |  |  | 1.6229 | 8.1399 | 96.2397 | 27.5
BRUME – BRUME SNCB 220.600 | 22T20211201E---B | ELIA | BRUME | BRUME SNCB | 220 | 1205.12 | 1140.56 | 1076 | 1140.56 | 1205.12 |  |  |  |  | 0.00484 | 0.0484 | 0 | 1
AWIRS – LE VAL 220.521 | 22T-BE-IN-LI025U | ELIA | AWIRS | LE VAL | 220 | 1223.04 | 1157.52 | 1092 | 1157.52 | 1223.04 |  |  |  |  | 0.33009 | 2.6402 | 18.6488 | 6.6
AWIRS – RIMIERE 220.535 | 22T-BE-IN-LI026S | ELIA | AWIRS | RIMIERE | 220 | 1093.12 | 1034.56 | 976 | 1034.56 | 1093.12 |  |  |  |  | 0.4719 | 3.1291 | 20.062 | 7.4
LE VAL – RIMIERE 220.522 | 22T-BE-IN-LI0300 | ELIA | LE VAL | RIMIERE | 220 | 1093.12 | 1034.56 | 976 | 1034.56 | 1093.12 |  |  |  |  | 0.76714 | 5.2901 | 37.4008 | 13.4
LE VAL – SERAING 220.523 | 22T-BE-IN-LI029M | ELIA | LE VAL | SERAING | 220 | 1161.44 | 1099.22 | 1037 | 1099.22 | 1161.44 |  |  |  |  | 0.16988 | 1.1698 | 8.1983 | 2.9
JUPILLE – ROMSEE 220.534 | 22T-BE-IN-LI028O | ELIA | JUPILLE | ROMSEE | 220 | 881.44 | 834.22 | 787 | 834.22 | 881.44 |  |  |  |  | 0.45012 | 2.1698 | 13 | 5
JUPILLE – RIMIERE 220.538 | 22T-BE-IN-LI027Q | ELIA | JUPILLE | RIMIERE | 220 | 1223.04 | 1157.52 | 1092 | 1157.52 | 1223.04 |  |  |  |  | 0.60579 | 4.5232 | 57.6417 | 20.193
AUBANGE – ST-MARD 220.516 | 22T-BE-IN-LI039J | ELIA | AUBANGE | ST-MARD | 220 | 996.8 | 943.4 | 890 | 943.4 | 996.8 |  |  |  |  | 1.6199 | 8.3979 | 59 | 21.1
ST-MARD – ST-MARD SNCB 220.602 | 22T20211201F---6 | ELIA | ST-MARD | ST-MARD SNCB | 220 | 11200 | 10600 | 10000 | 10600 | 11200 |  |  |  |  | 0.00484 | 0.0484 | 0 | 1
ST-MARD – ST-MARD SNCB 220.601 | 22T20211201G---1 | ELIA | ST-MARD | ST-MARD SNCB | 220 | 11200 | 10600 | 10000 | 10600 | 11200 |  |  |  |  | 0.00484 | 0.0484 | 0 | 1
ROUVROY – ST-MARD 220.518 | 22T20211201H---X | ELIA | ROUVROY | ST-MARD | 220 | 996.8 | 943.4 | 890 | 943.4 | 996.8 |  |  |  |  | 0.054208 | 0.28024 | 2 | 0.7
Y – SAINT-MARD (– AUBANGE – LATOUR) 220.515 | 22T-BE-IN-LI038L | ELIA | REPIQUAGE LATOUR 220kV | ST-MARD | 220 | 996.8 | 943.4 | 890 | 943.4 | 996.8 |  |  |  |  | 0.43076 | 2.223 | 15.6818 | 5.6
ROMSEE – ROMSEE SNCB 220.536 | 22T20211201I---S | ELIA | ROMSEE | ROMSEE SNCB | 220 | 11200 | 10600 | 10000 | 10600 | 11200 |  |  |  |  | 0.00484 | 0.0484 | 0 | 1
ROMSEE – ROMSEE SNCB 220.537 | 22T20211201J---N | ELIA | ROMSEE | ROMSEE SNCB | 220 | 1318.24 | 1247.62 | 1177 | 1247.62 | 1318.24 |  |  |  |  | 0.00484 | 0.0484 | 0 | 1
Q2 – MARCOURT (– BASTOGNE – RIMIERE – SENONCHAMPS – VILLEROUX) 220.501 | 22T-BE-IN-LI033V | ELIA | REPIQUAGE MARCOURT 220kV | MARCOURT | 220 | 1190.56 | 1126.78 | 1063 | 1126.78 | 1190.56 |  |  |  |  | 0.05082 | 0.18005 | 1.9587 | 0.6
Y – VILLEROUX (– HOUFFALIZE – BRUME) 220.504 | 22T-BE-IN-LI034T | ELIA | REPIQUAGE HOUFFALIZE 220kV | VILLEROUX | 220 | 1393.28 | 1318.64 | 1244 | 1318.64 | 1393.28 |  |  |  |  | 1.5101 | 7.5301 | 89.5992 | 25.5
AUBANGE – VILLEROUX 220.506 | 22T-BE-IN-LI035R | ELIA | AUBANGE | VILLEROUX | 220 | 1190.56 | 1126.78 | 1063 | 1126.78 | 1190.56 |  |  |  |  | 4.0119 | 14.1599 | 154.157 | 47.2
Q1 – VILLEROUX (– BASTOGNE – MARCOURT – RIMIERE – SENONCHAMPS) 220.501 | 22T-BE-IN-LI033V | ELIA | REPIQUAGE SENONCHAMPS 220kV | VILLEROUX | 220 | 1190.56 | 1126.78 | 1063 | 1126.78 | 1190.56 |  |  |  |  | 0.63017 | 2.1499 | 8.4917 | 2.6
Y – HOUFFALIZE (– BRUME – VILLEROUX) 220.504 | 22T-BE-IN-LI034T | ELIA | REPIQUAGE HOUFFALIZE 220kV | HOUFFALIZE | 220 | 1393.28 | 1318.64 | 1244 | 1318.64 | 1393.28 |  |  |  |  | 0.017908 | 0.089056 | 1.062 | 0.3
AUBANGE – BELVAL 220.511 | 22T201907101---C | ELIA | AUBANGE | BELVAL | 220 | [6 empty] | 1036.606 |  |  | 0.88088 | 6.171 | 42.9752 | 1
Y – AUBANGE (– LATOUR – SAINT-MARD) 220.515 | 22T-BE-IN-LI038L | ELIA | AUBANGE | REPIQUAGE LATOUR 220kV | 220 | 996.8 | 943.4 | 890 | 943.4 | 996.8 |  |  |  |  | 1.194 | 6.1691 | 43.4008 | 15.5
Y – LATOUR (– AUBANGE – SAINT-MARD) 220.515 | 22T-BE-IN-LI038L | ELIA | REPIQUAGE LATOUR 220kV | LATOUR | 220 | 996.8 | 943.4 | 890 | 943.4 | 996.8 |  |  |  |  | 0.015004 | 0.07986 | 0.56198 | 0.2
Q2 – RIMIERE (– BASTOGNE – MARCOURT – SENONCHAMPS – VILLEROUX) 220.501 | 22T-BE-IN-LI033V | ELIA | REPIQUAGE MARCOURT 220kV | RIMIERE | 220 | 1190.56 | 1126.78 | 1063 | 1126.78 | 1190.56 |  |  |  |  | 3.2302 | 11.3 | 124.1074 | 38
Q1 – Q2 (– BASTOGNE – MARCOURT – SENONCHAMPS – VILLEROUX) 220.501 | 22T-BE-IN-LI033V | ELIA | REPIQUAGE MARCOURT 220kV | REPIQUAGE SENONCHAMPS 220kV | 220 | 1190.56 | 1126.78 | 1063 | 1126.78 | 1190.56 |  |  |  |  | 2.2801 | 8.0402 | 87.5207 | 26.8
Y – ROMSEE (– SART-TILMAN – SERAING) 220.530 | 22T-BE-IN-LI031Z | ELIA | ROMSEE | REPIQUAGE SART-TILMAN 220kV | 220 | 1161.44 | 1099.22 | 1037 | 1099.22 | 1161.44 |  |  |  |  | 0.51624 | 3.6424 | 89.2139 | 9.56
OFFSHORE SWITCHYARD – STEVIN 220.4 O | 22T2019092022004 | ELIA | OFFSHORE SWITCHYARD | STEVIN | 220 | 1001 | 1001 | 1001 | 1001 | 1001 |  |  | 1001 | 1051.05 | 1.9939 | 4.5707 | 2884.342 | 40.87
STEVIN – OFFSHORE WINDPARK 220.1 O | 22T20211201K---I | ELIA | STEVIN | OFFSHORE WINDPARK | 220 | 1005 | 1005 | 1005 | 1005 | 1005 |  |  |  |  | 1.7681 | 5.5471 | 2699.132 | 45.4
Y – SERAING (– SERAING – SART-TILMAN) 220.530 | 22T-BE-IN-LI031Z | ELIA | REPIQUAGE SART-TILMAN 220kV | SERAING | 220 | 1161.44 | 1099.22 | 1037 | 1099.22 | 1161.44 |  |  |  |  | 0.32708 | 2.321 | 80.0717 | 6.29
STEVIN – OFFSHORE WINDPARK 220.3 O | 22T20211201L---D | ELIA | STEVIN | OFFSHORE WINDPARK | 220 | 1095 | 1095 | 1095 | 1095 | 1095 |  |  |  |  | 0.3332 | 2.9908 | 2445.416 | 28
JUPILLE – LIXHE 220.542 | 22T20210615----W | ELIA | JUPILLE | LIXHE | 220 | 995.68 | 942.34 | 889 | 942.34 | 995.68 |  |  |  |  | 1.4745 | 7.6213 | 54.4598 | 19.149
OFFSHORE SWITCHYARD – STEVIN 220.11 | 22T2019092022012 | ELIA | OFFSHORE SWITCHYARD | STEVIN | 220 | 1050 | 1050 | 1050 | 1050 | 1050 |  |  | 1050 | 1102.5 | 1.527 | 4.098 | 3122.743 | 40.917
OFFSHORE SWITCHYARD – OFFSHORE WINDPARK 220.13 | 22T20211201M---8 | ELIA | OFFSHORE SWITCHYARD | OFFSHORE WINDPARK | 220 | 1001 | 1001 | 1001 | 1001 | 1001 |  |  |  |  | 0.11398 | 0.50854 | 330.3782 | 4.384
OFFSHORE SWITCHYARD – OFFSHORE WINDPARK 220.14 | 22T20211201N---3 | ELIA | OFFSHORE SWITCHYARD | OFFSHORE WINDPARK | 220 | 1001 | 1001 | 1001 | 1001 | 1001 |  |  |  |  | 0.53973 | 2.408 | 1564.398 | 20.759
OFFSHORE SWITCHYARD – OFFSHORE WINDPARK 220.15 | 22T20211201O---Z | ELIA | OFFSHORE SWITCHYARD | OFFSHORE WINDPARK | 220 | 1001 | 1001 | 1001 | 1001 | 1001 |  |  |  |  | 0.35984 | 1.6054 | 1042.982 | 13.84
OFFSHORE SWITCHYARD – STEVIN 220.5 O | 22T20190920220-6 | ELIA | OFFSHORE SWITCHYARD | STEVIN | 220 | 1050 | 1050 | 1050 | 1050 | 1050 |  |  | 1050 | 1102.5 | 1.492 | 4.177 | 3129.521 | 40.866
OFFSHORE SWITCHYARD – OFFSHORE SWITCHYARD 220.6 O | 22T20190920227-M | ELIA | OFFSHORE SWITCHYARD | OFFSHORE SWITCHYARD | 220 | 1050 | 1050 | 1050 | 1050 | 1050 |  |  | 1050 | 1102.5 | 0.167 | 0.449 | 326.2311 | 4.26
Y – SART-TILMAN (– ROMSEE – SERAING) 220.530 | 22T-BE-IN-LI031Z | ELIA | SART-TILMAN | REPIQUAGE SART-TILMAN 220kV | 220 | 1161 | 1161 | 1161 | 1161 | 1161 |  |  |  |  | 0.0236 | 0.1672 | 1.52 | 0.4
220 kV Konjsko - Bilice 271/1 | 31T-0000-A-0023V | HOPS | Konjsko | Bilice | 220 | [6 empty] | 780 |  |  | 4.3 | 22.09 | 143.9 | 53.13
220 kV Konjsko - Bilice 271/2 | 31T-0000-A-0024T | HOPS | Konjsko | Bilice | 220 | [6 empty] | 780 |  |  | 4.3 | 22.09 | 143.9 | 53.13
220 kV Zakucac - Bilice 257 | 31T-0000-A-0022X | HOPS | Zakucac | Bilice | 220 | [6 empty] | 780 |  |  | 6.22 | 30.75 | 202.5 | 75.2
220 kV Mraclin -Brinje 208 | 31T-0000-A-0007T | HOPS | Mraclin | Brinje | 220 | [6 empty] | 1210 |  |  | 7.07 | 37.7 | 414.66 | 117.8
220 kV Senj - Brinje 235 | 31T-0000-A-0013Y | HOPS | Senj | Brinje | 220 | [6 empty] | 815 |  |  | 1.24 | 6.66 | 41.62 | 15.53
220 kV Brinje - VE Padene | 31T-0000-A-00200 | HOPS | Brinje | VE Padene | 220 | [6 empty] | 780 |  |  | 11.59 | 60.82 | 392.46 | 144.82
400 kV Zerjavinec - Ernestinovo 408 | 31T-0000-A-00022 | HOPS | Zerjavinec | Ernestinovo | 400 | [6 empty] | 1920 |  |  | 7.17 | 76.29 | 816.28 | 231.2
400 kV Konjsko - Velebit 419 | 31T-0000-A-0008R | HOPS | Konjsko | Velebit | 400 | [6 empty] | 1600 |  |  | 3.22 | 33.6 | 354.46 | 100.827
220 kV Konjsko - VE Padene | 31T-0000-A-0021Z | HOPS | Konjsko | VE Padene | 220 | [6 empty] | 780 |  |  | 5.26 | 27.62 | 178.21 | 65.76
220 kV Zakucac - Konjsko 274 | 31T-0000-A-00111 | HOPS | Zakucac | Konjsko | 220 | [6 empty] | 1200 |  |  | 1.57 | 5.24 | 67.54 | 24.92
220 kV TE Sisak - Meduric 246 | 31T-0000-A-0006V | HOPS | TE Sisak | Meduric | 220 | [6 empty] | 815 |  |  | 3.64 | 18.45 | 122.85 | 45
400 kV Tumbri - Melina 456 | 31T-0000-A-00014 | HOPS | Tumbri | Melina | 400 | [6 empty] | 1920 |  |  | 3.83 | 42.08 | 448.75 | 127.56
400 kV Melina - Velebit 434 | 31T-0000-A-0009P | HOPS | Melina | Velebit | 400 | [6 empty] | 1920 |  |  | 5.88 | 61.08 | 629.38 | 178.8
220 kV Melina - Pehlin1 285 | 31T-0000-A-0016S | HOPS | Melina | Pehlin | 220 | [6 empty] | 815 |  |  | 1.18 | 5.95 | 38.05 | 13.69
220 kV Melina - Pehlin2 286/2 | 31T-0000-A-0017Q | HOPS | Melina | Pehlin | 220 | [6 empty] | 960 |  |  | 1.1 | 7.2 | 49.88 | 17.94
220 kV Melina - Senj 241 | 31T-0000-A-0018O | HOPS | Melina | Senj | 220 | [6 empty] | 815 |  |  | 4.42 | 23.69 | 147.49 | 55.24
220 kV Melina - Plomin 287 | 31T-0000-A-0015U | HOPS | Melina | Plomin | 220 | [6 empty] | 950 |  |  | 3.72 | 25.6 | 178.37 | 64.16
220 kV Mraclin - TE Sisak 249 | 31T-0000-A-0005X | HOPS | Mraclin | TE Sisak | 220 | [6 empty] | 780 |  |  | 3.56 | 18.44 | 120.12 | 44
220 kV Mraclin - TE Sisak2 222 | 31T-0000-A-0019M | HOPS | Mraclin | TE Sisak | 220 | [6 empty] | 780 |  |  | 4.69 | 24.75 | 178.66 | 58.637
220 kV Zerjavinec - Mraclin 247 | 31T-0000-A-0004Z | HOPS | Zerjavinec | Mraclin | 220 | [6 empty] | 780 |  |  | 2.11 | 10.82 | 73.39 | 26.4
220 kV Pehlin - Plomin 284 | 31T-0000-A-0014W | HOPS | Pehlin | Plomin | 220 | [6 empty] | 950 |  |  | 2.73 | 19.04 | 129.41 | 46.22
400 kV Zerjavinec - Tumbri 477 | 31T-0000-A-00030 | HOPS | Zerjavinec | Tumbri | 400 | [6 empty] | 1900 |  |  | 1.83 | 19.03 | 211.06 | 61
Albertirsa - God | 15T-M0000003237K | MAVIR | Albertirsa | God | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.474 | 18.066 | 262.6371 | 65.22
Albertirsa - Jozsa | 15T-M0000003425J | MAVIR | Albertirsa | Jozsa | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 2.4697 | 47.4811 | 659.3261 | 168
Albertirsa - Kerepes | 15T-M0000003238I | MAVIR | Albertirsa | Kerepes | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 0.963 | 11.804 | 171.531 | 42.6
Albertirsa - Martonvasar | 15T-M0000003351M | MAVIR | Albertirsa | Martonvasar | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.722 | 20.505 | 250.3221 | 67.47
Albertirsa - Szigetcsep | 15T-M0000003335K | MAVIR | Albertirsa | Szigetcsep | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.399 | 16.149 | 192.5796 | 52.6
Albertirsa - Szolnok | 15T-M0000002902G | MAVIR | Albertirsa | Szolnok | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.332 | 15.442 | 150.7964 | 46.16
Bekescsaba - Sandorfalva | 15T-M00000001283 | MAVIR | Bekescsaba | Sandorfalva | 400 | 1600 | 1600 | 1600 | 1600 | [5 empty] | 2.61 | 29.08 | 325.8774 | 92.01
Bekescsaba - Szolnok | 15T-M0000002903E | MAVIR | Bekescsaba | Szolnok | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 3.119 | 38.623 | 377.3053 | 113.3
Bicske Del - Gonyu | 15T-M00000029351 | MAVIR | Bicske Del | Gonyu | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 3.0888 | 33.7584 | 386.6283 | 107.8
Bicske Del - Martonvasar | 15T-M00000030240 | MAVIR | Bicske Del | Martonvasar | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 0.51241 | 5.7409 | 129.8446 | 24.54
Dunamenti - Oroszlany | 15T-M0000000303B | MAVIR | Dunamenti | Oroszlany | 220 | 800 | 730 | 640 | 730 | [5 empty] | 2.8184 | 21.1427 | 196.9532 | 60.2
God - Kerepes | 15T-M0000003239G | MAVIR | God | Kerepes | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 0.522 | 6.401 | 92.9911 | 23.1
God - Sajoszoged | 15T-M00000004029 | MAVIR | God | Sajoszoged | 400 | 1600 | 1600 | 1600 | 1600 | [5 empty] | 4.06 | 42.24 | 551.6637 | 144.81
Gonyu - Gyor | 15T-M000002791-J | MAVIR | Gonyu | Gyor | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 0.424 | 4.628 | 53.0929 | 14.8
Gyor - Liter | 15T-M00000004231 | MAVIR | Gyor | Liter | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 2.1287 | 24.4704 | 253.109 | 74.3
Gyor - Oroszlany | 15T-M00000004207 | MAVIR | Gyor | Oroszlany | 220 | 1000 | 1000 | 1000 | 1000 | [5 empty] | 1.4325 | 15.4462 | 174.1385 | 48.9
Gyor - Szombathely | 15T-M0000002523O | MAVIR | Gyor | Szombathely | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 3.11 | 35.2 | 322.3274 | 112.7
Heviz - Liter | 15T-M00000004995 | MAVIR | Heviz | Liter | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 2.81 | 28.74 | 313.8451 | 89.6
Heviz - Szombathely 1 | 15T-M00000027650 | MAVIR | Heviz | Szombathely 1 | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 2.23 | 24.42 | 278.4079 | 77.8
Heviz - Szombathely 2 | 15T-M0000002766Z | MAVIR | Heviz | Szombathely 2 | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 2.23 | 24.42 | 278.4079 | 77.8
Heviz - Toponar | 15T-M00000004979 | MAVIR | Heviz | Toponar | 400 | 1600 | 1600 | 1600 | 1600 | [5 empty] | 3.23 | 33.13 | 361.9115 | 103.79
Jozsa - Sajoszoged | 15T-M0000003052W | MAVIR | Jozsa | Sajoszoged | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.6611 | 19.626 | 192.4847 | 58.08
Kisvarda - Sajoszoged | 15T-M0000000692B | MAVIR | Kisvarda | Sajoszoged | 220 | 600 | 600 | 600 | 600 | [5 empty] | 7.16 | 40.57 | 258.5531 | 96.41
Liter - Martonvasar | 15T-M0000000780E | MAVIR | Liter | Martonvasar | 400 | 2000 | 2000 | 1800 | 2000 | [5 empty] | 2.03 | 24.3 | 236.2478 | 71.1
Liter - Paks | 15T-M0000000781C | MAVIR | Liter | Paks | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 4.72 | 32.89 | 318.5575 | 96.57
Martonvasar - Perkata | 15T-M0000003193E | MAVIR | Martonvasar | Perkata | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 0.6944 | 11.0587 | 133.6434 | 36.42
Martonvasar - Szigetcsep | 15T-M0000003336I | MAVIR | Martonvasar | Szigetcsep | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 0.452 | 5.767 | 73.8274 | 19.5
Paks - Pecs 1 | 15T-M0000002266I | MAVIR | Paks | Pecs 1 | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 2.384 | 25.607 | 233.1062 | 81.63
Paks - Pecs 2 | 15T-M0000002267G | MAVIR | Paks | Pecs 2 | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 2.384 | 25.607 | 233.1062 | 81.63
Paks - Perkata | 15T-M0000003194C | MAVIR | Paks | Perkata | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.13 | 17.9973 | 217.4925 | 59.27
Paks - Sandorfalva | 15T-M00000010193 | MAVIR | Paks | Sandorfalva | 400 | 1600 | 1600 | 1600 | 1600 | [5 empty] | 3.21 | 37.99 | 372.907 | 112.32
Paks - Toponar | 15T-M0000001020I | MAVIR | Paks | Toponar | 400 | 1600 | 1600 | 1600 | 1600 | [5 empty] | 2.63 | 30.79 | 308.1902 | 91.9
Sajoszoged - Tiszalok | 15T-M0000001128Z | MAVIR | Sajoszoged | Tiszalok | 220 | 600 | 600 | 600 | 600 | [5 empty] | 2.37 | 12.57 | 79.7965 | 29.9
Szabolcsbaka - Jozsa | 15T-M0000003424L | MAVIR | Szabolcsbaka | Jozsa | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.2002 | 22.9991 | 318.9659 | 81.32
Sajoszoged - Detk I. | 15T-M00000002433 | MAVIR | Sajoszoged | Detk | 220 | 600 | 600 | 600 | 600 | [5 empty] | 6.04 | 26.86 | 254.469 | 78
Sajoszoged - Detk II. | 15T-M00000002441 | MAVIR | Sajoszoged | Detk | 220 | 600 | 600 | 600 | 600 | [5 empty] | 5.65 | 29.44 | 190.6947 | 70.7
Detk - Szolnok | 15T-M000000245-R | MAVIR | Detk | Szolnok | 220 | 900 | 900 | 900 | 900 | [5 empty] | 3.69 | 27.09 | 172.4734 | 64.5
Detk - Zugló I. | 15T-M0000000246Y | MAVIR | Detk | Zuglo | 220 | 820 | 730 | 640 | 730 | [5 empty] | 7.1 | 30.92 | 221.1681 | 92.61
Detk - Zugló II. | 15T-M0000000247W | MAVIR | Detk | Zuglo | 220 | 820 | 730 | 640 | 730 | [5 empty] | 6.74 | 35.08 | 227.7655 | 84.5
Dunamenti - Martonvasar I. | 15T-M0000000299D | MAVIR | Dunamenti | Martonvasar | 220 | 1360 | 1240 | 1120 | 1240 | [5 empty] | 0.42 | 3.03 | 19.792 | 7.24
Dunamenti - Martonvasar II. | 15T-M0000000300H | MAVIR | Dunamenti | Martonvasar | 220 | 1360 | 1240 | 1120 | 1240 | [5 empty] | 0.42 | 3.03 | 19.792 | 7.26
Dunamenti - Ocsa I. | 15T-M0000000301F | MAVIR | Dunamenti | Ocsa | 220 | 1460 | 1300 | 1140 | 1300 | [5 empty] | 1.69 | 8.78 | 103.9867 | 28.29
Dunamenti - Ocsa II. | 15T-M0000000302D | MAVIR | Dunamenti | Ocsa | 220 | 1460 | 1300 | 1140 | 1300 | [5 empty] | 1.69 | 8.78 | 103.9867 | 28.23
God - Zuglo | 15T-M0000002407Q | MAVIR | God | Zuglo | 220 | 600 | 600 | 600 | 600 | [5 empty] | 1.64 | 6.89 | 69.115 | 20.95
Ocsa - Zuglo | 15T-M00000009547 | MAVIR | Ocsa | Zuglo | 220 | 1200 | 1200 | 1140 | 1200 | [5 empty] | 2.99 | 15.63 | 185.9823 | 51.65
Sajoszoged - Szolnok | 15T-M00000011270 | MAVIR | Sajoszoged | Szolnok | 220 | 600 | 600 | 600 | 600 | [5 empty] | 9.42 | 50.09 | 296.2522 | 114.77
Sajoszoged - Felsozsolca I. | 15T-M0000000370X | MAVIR | Sajoszoged | Felsozsolca | 400 | 1600 | 1600 | 1600 | 1600 | [5 empty] | 0.72 | 8.45 | 84.19 | 25.17
Sajoszoged - Felsozsolca II. | 15T-M0000000371V | MAVIR | Sajoszoged | Felsozsolca | 400 | 1600 | 1600 | 1600 | 1600 | [5 empty] | 0.72 | 8.44 | 84.19 | 25.12
Felsozsolca - Sajoivanka | 15T-M0000000369I | MAVIR | Felsozsolca | Sajoivanka | 400 | 1600 | 1600 | 1600 | 1600 | [5 empty] | 0.82 | 9.72 | 96.76 | 28.89
Buj - Sajoszoged | 15T-M0000003788K | MAVIR | Buj | Sajoszoged | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.3321 | 16.4651 | 206.4026 | 55.22
Szabolcsbaka - Buj | 15T-M0000003787M | MAVIR | Szabolcsbaka | Buj | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.102 | 13.1612 | 163.2686 | 43.89
PIASECZNO-KOZIENICE | 19T1100000066830 | PSE | PIASECZNO | KOZIENICE | 220 | 1345 | 1312.5 | 1280 | 1312.5 |  |  |  | 1195 | 1410 | 5.808 | 35.579 | 251.1983 | 88.8
JOACHIMOW-ROGOWIEC | 14T-220-0-002027 | PSE | JOACHIMOW | ROGOWIEC | 220 | 995 | 942.5 | 890 | 942.5 |  |  |  | 750 | 1100 | 4.448 | 32.021 | 215.9504 | 78.1
JOACHIMOW-ROGOWIEC | 19T110000006684Z | PSE | JOACHIMOW | ROGOWIEC | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 3.9785 | 28.111 | 201.5289 | 70.6
SOCHACZEW-KONIN | 19T110000006685X | PSE | SOCHACZEW | KONIN | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 8.2183 | 60.302 | 404.3388 | 146.3
ZGIERZ-ADAMOW | 19T110000006686V | PSE | ZGIERZ | ADAMOW | 220 | 645 | 587.5 | 530 | 587.5 |  |  |  | 370 | 760 | 6.3114 | 33.27 | 208.5537 | 78.3
PABIANICE-ADAMOW | 14T-221-0-00206Q | PSE | PABIANICE | ADAMOW | 220 | 895 | 847.5 | 800 | 847.5 |  |  |  | 675 | 990 | 5.1594 | 30.792 | 190.3512 | 72
PODOLSZYCE-PATNOW | 14T-220-0-00207Y | PSE | PODOLSZYCE | PATNOW | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 6.9502 | 51.928 | 332.2521 | 123.4
LOSNICE-KIELCE | 14T-220-0-00208W | PSE | LOSNICE | KIELCE | 220 | 645 | 587.5 | 530 | 587.5 |  |  |  | 370 | 760 | 7.3084 | 40.869 | 242.1074 | 93.5
JOACHIMOW-KIELCE | 19T110000006687T | PSE | JOACHIMOW | KIELCE | 220 | 895 | 847.5 | 800 | 847.5 |  |  |  | 675 | 990 | 5.8903 | 35.511 | 218.0372 | 82.7
GROSZOWICE-ZABKOWICE | 19T000000000448S | PSE | GROSZOWICE | ZABKOWICE | 220 | 1005 | 947.5 | 890 | 947.5 |  |  |  | 735 | 1120 | 5.2901 | 39.528 | 258.0579 | 94.8
BYDGOSZCZ ZA-PILA KRZEWINA | 19T110000006455D | PSE | BYDGOSZCZ ZA | PILA KRZEWINA | 220 | 1500 | 1500 | 1500 | 1500 |  |  |  | 1500 | 1500 | 2.3184 | 24.21 | 325.0207 | 82.8
BYDGOSZCZ ZA-PILA KRZEWINA | 19T110000006456B | PSE | BYDGOSZCZ ZA | PILA KRZEWINA | 220 | 1500 | 1500 | 1500 | 1500 |  |  |  | 1500 | 1500 | 2.3184 | 24.219 | 325.2066 | 82.8
PATNOW-WLOCLAWEK AZ | 19T000000000449Q | PSE | PATNOW | WLOCLAWEK AZ | 220 | 850 | 800 | 750 | 800 |  |  |  | 615 | 950 | 5.4111 | 32.481 | 195.9091 | 75
JASINIEC-PATNOW | 19T0000000004504 | PSE | JASINIEC | PATNOW | 220 | 940 | 885 | 830 | 885 |  |  |  | 680 | 1050 | 8.14 | 43.12 | 268.46 | 100.6
PILA KRZEWINA-ZYDOWO | 19T000000006401O | PSE | PILA KRZEWINA | ZYDOWO | 220 | 705 | 642.5 | 580 | 642.5 |  |  |  | 405 | 720 | 7.3423 | 48.1 | 299.4215 | 112.8
MORY-KOZIENICE | 14T-220-0-002205 | PSE | MORY | KOZIENICE | 220 | 1585.1 | 1557.6 | 1530.1 | 1557.6 |  |  |  | 1455 | 1600 | 7.0712 | 37.428 | 263.1198 | 93.2
OSTROLEKA-OLSZTYN | 19T000000000456T | PSE | OSTROLEKA | OLSZTYN | 220 | 1190 | 1140 | 1090 | 1140 |  |  |  | 960 | 1290 | 3.4316 | 34.582 | 329.5248 | 123.5
POLANIEC-KLIKOWA | 14T-220-0-002221 | PSE | POLANIEC | KLIKOWA | 220 | 1250 | 1250 | 1250 | 1250 |  |  |  | 1250 | 1250 | 1.8005 | 20.918 | 223.9256 | 64
DOBRZEN-PASIKUROWICE | 19T000000000377P | PSE | DOBRZEN | PASIKUROWICE | 400 | 1700 | 1600 | 1500 | 1600 |  |  |  | 1230 | 1900 | 3.056 | 32.4 | 339.8813 | 98.2
MILOSNA-KOZIENICE | 19T110000006688R | PSE | MILOSNA | KOZIENICE | 400 | 2010 | 1895 | 1780 | 1895 |  |  |  | 1470 | 2240 | 2.4 | 24.096 | 252 | 71.8
POLANIEC-TARNOW | 19T000000006396S | PSE | POLANIEC | TARNOW | 400 | 1500 | 1500 | 1359 | 1500 |  |  |  | 950 | 1250 | 2.704 | 31.2 | 337.5625 | 96
JOACHIMOW-ROGOWIEC | 19T110000006689P | PSE | JOACHIMOW | ROGOWIEC | 400 | 2000 | 2000 | 1900.7 | 2000 |  |  |  | 1610 | 2000 | 2.192 | 25.104 | 273.4 | 78
TUCZNAWA-ROGOWIEC | 19T0000000064292 | PSE | TUCZNAWA | ROGOWIEC | 400 | 2000 | 2000 | 1900.7 | 2000 |  |  |  | 1610 | 2000 | 3.744 | 43.264 | 468.2375 | 133.1
GRUDZIADZ-PLOCK | 19T000000000291Z | PSE | GRUDZIADZ | PLOCK | 400 | 2000 | 1894.4 | 1779.6 | 1894.4 |  |  |  | 1470 | 2000 | 3.472 | 40.208 | 419.3625 | 121.5
RZESZOW-TARNOW | 19T110000006445G | PSE | RZESZOW | TARNOW | 400 | 1200 | 1200 | 1200 | 1200 |  |  |  | 950 | 1200 | 2.416 | 28.112 | 301.1812 | 86.1
TREBACZEW-DOBRZEN | 19T110000006442M | PSE | TREBACZEW | DOBRZEN | 400 | 1410 | 1285 | 1160 | 1285 |  |  |  | 810 | 1660 | 5.68 | 57.872 | 599.3375 | 175.1
TARNOW-KROSNO ISKRZYNIA | 19T000000000296P | PSE | TARNOW | KROSNO ISKRZYNIA | 400 | 2000 | 2000 | 2000 | 2000 |  |  |  | 1920 | 2000 | 2.304 | 23.136 | 320.0813 | 82
OSTROW WLKP-ROGOWIEC | 19T1100000066903 | PSE | OSTROW WLKP | ROGOWIEC | 400 | 2000 | 2000 | 2000 | 2000 |  |  |  | 1840 | 2000 | 3.52 | 37.664 | 479.4625 | 125.4
OSTROW WLKP-TREBACZEW | 19T1100000066911 | PSE | OSTROW WLKP | TREBACZEW | 400 | 2300 | 2200 | 2100 | 2200 |  |  |  | 1840 | 2500 | 3.648 | 39.248 | 496.4 | 130.5
MORZYCZYN-DUNOWO | 19T000000000299J | PSE | MORZYCZYN | DUNOWO | 400 | 1660 | 1510 | 1360 | 1510 |  |  |  | 950 | 1960 | 3.6 | 42.352 | 441.3375 | 127.9
TREBACZEW-JOACHIMOW | 19T110000006443K | PSE | TREBACZEW | JOACHIMOW | 400 | 1410 | 1285 | 1160 | 1285 |  |  |  | 810 | 1660 | 1.936 | 19.84 | 205.5188 | 59.7
KOZIENICE-STANISLAWOW | 19T000000006424C | PSE | KOZIENICE | STANISLAWOW | 400 | 2760 | 2655 | 2550 | 2655 |  |  |  | 2280 | 2970 | 2.864 | 31.856 | 422.1 | 108.2
RZESZOW-SKAWINA | 19T000000006400Q | PSE | RZESZOW | SKAWINA | 400 | 1660 | 1510 | 1360 | 1510 |  |  |  | 950 | 1960 | 5.296 | 61.152 | 664.1375 | 188.5
DOBRZEN-PASIKUROWICE | 19T0000000063911 | PSE | DOBRZEN | PASIKUROWICE | 400 | 2000 | 2000 | 2000 | 2000 |  |  |  | 1845 | 2000 | 3.104 | 32.976 | 431.5188 | 111.3
DOBRZEN-WROCLAW | 19T000000006412J | PSE | DOBRZEN | WROCLAW | 400 | 1200 | 1200 | 1200 | 1200 |  |  |  | 1200 | 1200 | 2.544 | 27.024 | 353.5187 | 91.3
OSTROLEKA-OLSZTYN-MATK | 19T000000006369V | PSE | OSTROLEKA | OLSZTYN-MATK | 400 | 2400 | 2400 | 2400 | 2400 |  |  |  | 2280 | 2400 | 3.696 | 37.856 | 527.7188 | 136.1
KOZIENICE-SIEDLCE UJRZANOW | 19T0000000063717 | PSE | KOZIENICE | SIEDLCE UJRZANOW | 400 | 2760 | 2655 | 2550 | 2655 |  |  |  | 2280 | 2970 | 2.576 | 27.136 | 357.7812 | 98.8
PATNOW-JASINIEC | 19T110000006438D | PSE | PATNOW | JASINIEC | 400 | 3000 | 3000 | 3000 | 3000 |  |  |  | 2397 | 3000 | 2.416 | 30.256 | 397.5625 | 101
JANOW-PIOTRKOW | 19T110000006693Y | PSE | JANOW | PIOTRKOW | 220 | 1005 | 947.5 | 890 | 947.5 |  |  |  | 735 | 1120 | 2.2119 | 16.219 | 108.3678 | 39.2
MILOSNA-OSTROLEKA | 19T000000000486K | PSE | MILOSNA | OSTROLEKA | 220 | 1005 | 947.5 | 890 | 947.5 |  |  |  | 735 | 1120 | 7.54 | 56.64 | 358.06 | 126.2
MORY-PODOLSZYCE | 19T110000006694W | PSE | MORY | PODOLSZYCE | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 6.1081 | 45.138 | 295.9298 | 108.6
JANOW-ROGOWIEC | 19T110000006695U | PSE | JANOW | ROGOWIEC | 220 | 885 | 847.5 | 810 | 847.5 |  |  |  | 910 | 1110 | 4.4722 | 24.452 | 159.0702 | 58.7
ELK-OSTROLEKA | 19T000000000489E | PSE | ELK | OSTROLEKA | 220 | 720 | 720 | 679.6 | 720 |  |  |  | 475 | 720 | 5.1691 | 38.41 | 251.1364 | 91.9
PABIANICE-ROGOWIEC | 19T110000006696S | PSE | PABIANICE | ROGOWIEC | 220 | 1200 | 1150 | 1100 | 1150 |  |  |  | 970 | 1250 | 2.8314 | 19.491 | 147.9545 | 50.2
PABIANICE-ROGOWIEC | 19T110000006696S | PSE | PABIANICE | ROGOWIEC | 220 | 1200 | 1150 | 1100 | 1150 |  |  |  | 970 | 1250 | 2.8314 | 19.491 | 147.9545 | 50.2
PABIANICE-ROGOWIEC | 19T110000006698O | PSE | PABIANICE | ROGOWIEC | 220 | 1200 | 1150 | 1100 | 1150 |  |  |  | 970 | 1300 | 2.8314 | 19.491 | 147.9545 | 50.2
OLTARZEW-JANOW | 19T110000006699M | PSE | OLTARZEW | JANOW | 220 | 995 | 942.5 | 890 | 942.5 |  |  |  | 750 | 1100 | 5.7402 | 43.149 | 261.5909 | 99.9
MORY-OLTARZEW | 19T110000006700Q | PSE | MORY | OLTARZEW | 220 | 1190 | 1140 | 1090 | 1140 |  |  |  | 960 | 1250 | 0.6486 | 4.8013 | 31.405 | 11.5
OLTARZEW-MORY | 19T110000006701O | PSE | OLTARZEW | MORY | 220 | 1120 | 1075 | 1030 | 1075 |  |  |  | 910 | 1210 | 0.5711 | 4.2689 | 25.8264 | 9.9
SOCHACZEW-OLTARZEW | 19T110000006702M | PSE | SOCHACZEW | OLTARZEW | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 1.9989 | 14.931 | 96.1983 | 35.6
MORY-PRAGA | 19T110000006803G | PSE | MORY | PRAGA | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 1.8 | 13.381 | 87.52 | 32
PRAGA-MILOSNA | 19T110000006804E | PSE | PRAGA | MILOSNA | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 1.352 | 10.049 | 66 | 24
MORY-PIASECZNO | 19T110000006704I | PSE | MORY | PIASECZNO | 220 | 1250 | 1250 | 1250 | 1250 |  |  |  | 1195 | 1250 | 1.8489 | 12.269 | 87.6446 | 30.8
JANOW-ZGIERZ | 19T110000006705G | PSE | JANOW | ZGIERZ | 220 | 943 | 904.5 | 866 | 904.5 |  |  |  | 768 | 1020 | 2.3184 | 12.928 | 82.314 | 30.6
JANOW-PABIANICE | 19T110000006706E | PSE | JANOW | PABIANICE | 220 | 885 | 847.5 | 810 | 847.5 |  |  |  | 710 | 960 | 1.3891 | 8.0876 | 50.9711 | 19
PIOTRKOW-ROGOWIEC | 19T110000006707C | PSE | PIOTRKOW | ROGOWIEC | 220 | 1154.9 | 1102.4 | 1049.9 | 1102.4 |  |  |  | 920 | 1200 | 1.9312 | 14.041 | 99.3388 | 33.8
PIOTRKOW-ROGOWIEC | 19T110000006707C | PSE | PIOTRKOW | ROGOWIEC | 220 | 1154.9 | 1102.4 | 1049.9 | 1102.4 |  |  |  | 920 | 1200 | 1.9312 | 14.041 | 99.3388 | 33.8
PULAWY-ROZKI | 19T1100000067098 | PSE | PULAWY | ROZKI | 220 | 705 | 642.5 | 580 | 642.5 |  |  |  | 405 | 830 | 5.1014 | 29.771 | 192.2727 | 70.8
POLANIEC-RADKOWICE | 19T110000006710N | PSE | POLANIEC | RADKOWICE | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 4.3802 | 32.539 | 212.7273 | 77.8
ABRAMOWICE-STALOWA WOLA | 19T110000006711L | PSE | ABRAMOWICE | STALOWA WOLA | 220 | 895 | 847.5 | 800 | 847.5 |  |  |  | 675 | 990 | 5.9919 | 36.61 | 226.9835 | 85.7
ABRAMOWICE-MOKRE | 19T110000006712J | PSE | ABRAMOWICE | MOKRE | 220 | 895 | 847.5 | 800 | 847.5 |  |  |  | 675 | 990 | 5.1788 | 32.08 | 223.657 | 78.5
KOZIENICE-PULAWY | 19T110000006713H | PSE | KOZIENICE | PULAWY | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 2.6281 | 18.068 | 137.7686 | 46.7
KOZIENICE-PULAWY | 19T110000006713H | PSE | KOZIENICE | PULAWY | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 2.6281 | 18.068 | 137.7686 | 46.7
KOZIENICE-PULAWY | 19T110000006715D | PSE | KOZIENICE | PULAWY | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 2.6281 | 18.068 | 137.7686 | 46.7
KOZIENICE-PULAWY | 19T110000006715D | PSE | KOZIENICE | PULAWY | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 2.6281 | 18.068 | 137.7686 | 46.7
ABRAMOWICE-PULAWY | 19T1100000067179 | PSE | ABRAMOWICE | PULAWY | 220 | 995 | 942.5 | 890 | 942.5 |  |  |  | 750 | 1100 | 3.1799 | 23.28 | 150.2066 | 55.3
ABRAMOWICE-PULAWY | 19T1100000067179 | PSE | ABRAMOWICE | PULAWY | 220 | 995 | 942.5 | 890 | 942.5 |  |  |  | 750 | 1100 | 3.1799 | 23.28 | 150.2066 | 55.3
MOKRE-ZAMOSC | 19T000000006422G | PSE | MOKRE | ZAMOSC | 220 | 895 | 847.5 | 800 | 847.5 |  |  |  | 675 | 990 | 1.4617 | 9.7284 | 63.4091 | 23.2
CHELM-MOKRE | 19T1100000067195 | PSE | CHELM | MOKRE | 220 | 600 | 600 | 600 | 600 |  |  |  | 475 | 600 | 3.388 | 24.868 | 167.0248 | 60.3
CHELM-MOKRE | 19T1100000067195 | PSE | CHELM | MOKRE | 220 | 600 | 600 | 600 | 600 |  |  |  | 475 | 600 | 3.388 | 24.868 | 167.0248 | 60.3
POLANIEC-CHMIELOW | 19T110000006721I | PSE | POLANIEC | CHMIELOW | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 1.5924 | 12.129 | 90.7025 | 30.7
POLANIEC-CHMIELOW | 19T110000006721I | PSE | POLANIEC | CHMIELOW | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 1.5924 | 12.129 | 90.7025 | 30.7
BOGUCHWALA-CHMIELOW | 19T110000006723E | PSE | BOGUCHWALA | CHMIELOW | 220 | 900 | 900 | 900 | 900 |  |  |  | 805 | 1170 | 3.8188 | 28.401 | 185.6405 | 67.9
BOGUCHWALA-CHMIELOW | 19T110000006723E | PSE | BOGUCHWALA | CHMIELOW | 220 | 900 | 900 | 900 | 900 |  |  |  | 805 | 1170 | 3.8188 | 28.401 | 185.6405 | 67.9
CHMIELOW-POLANIEC | 19T110000006725A | PSE | CHMIELOW | POLANIEC | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 2.7007 | 19.66 | 134.1116 | 49.4
CHMIELOW-POLANIEC | 19T110000006725A | PSE | CHMIELOW | POLANIEC | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 2.7007 | 19.66 | 134.1116 | 49.4
CHMIELOW-STALOWA WOLA | 19T1100000067276 | PSE | CHMIELOW | STALOWA WOLA | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 2.7394 | 20.551 | 130.7025 | 48.7
CHMIELOW-STALOWA WOLA | 19T1100000067276 | PSE | CHMIELOW | STALOWA WOLA | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 2.7394 | 20.551 | 130.7025 | 48.7
KOZIENICE-ROZKI | 19T1100000067292 | PSE | KOZIENICE | ROZKI | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 2.9911 | 21.069 | 158.0372 | 53.1
KOZIENICE-ROZKI | 19T1100000067292 | PSE | KOZIENICE | ROZKI | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 2.9911 | 21.069 | 158.0372 | 53.1
KOZIENICE-ROZKI | 19T110000006731F | PSE | KOZIENICE | ROZKI | 220 | 645 | 587.5 | 530 | 587.5 |  |  |  | 370 | 760 | 2.9911 | 21.069 | 158.0372 | 53.1
KOZIENICE-ROZKI | 19T110000006731F | PSE | KOZIENICE | ROZKI | 220 | 645 | 587.5 | 530 | 587.5 |  |  |  | 370 | 760 | 2.9911 | 21.069 | 158.0372 | 53.1
KIELCE-ROZKI | 19T110000006733B | PSE | KIELCE | ROZKI | 220 | 828 | 784.5 | 741 | 784.5 |  |  |  | 626 | 915 | 6.021 | 31.499 | 186.9421 | 72.2
KIELCE-ROZKI | 19T110000006733B | PSE | KIELCE | ROZKI | 220 | 828 | 784.5 | 741 | 784.5 |  |  |  | 626 | 915 | 6.021 | 31.499 | 186.9421 | 72.2
KIELCE-RADKOWICE | 19T1100000067357 | PSE | KIELCE | RADKOWICE | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 1.1906 | 8.8378 | 57.8099 | 21.1
KIELCE-RADKOWICE | 19T1100000067357 | PSE | KIELCE | RADKOWICE | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 1.1906 | 8.8378 | 57.8099 | 21.1
KIELCE-KIELCE PIASKI | 19T1100000067373 | PSE | KIELCE | KIELCE PIASKI | 220 | 720 | 720 | 720 | 720 |  |  |  | 675 | 720 | 1.1713 | 7.41 | 46.4669 | 17.2
KIELCE-KIELCE PIASKI | 19T1100000067373 | PSE | KIELCE | KIELCE PIASKI | 220 | 720 | 720 | 720 | 720 |  |  |  | 675 | 720 | 1.1713 | 7.41 | 46.4669 | 17.2
KIELCE PIASKI-RADKOWICE | 19T110000006740E | PSE | KIELCE PIASKI | RADKOWICE | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 730 | 1170 | 1.1858 | 8.8185 | 61.7355 | 21
KIELCE PIASKI-RADKOWICE | 19T110000006740E | PSE | KIELCE PIASKI | RADKOWICE | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 730 | 1170 | 1.1858 | 8.8185 | 61.7355 | 21
WIELOPOLE-KEDZIERZYN | 19T000000000469K | PSE | WIELOPOLE | KEDZIERZYN | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 2.3619 | 16.272 | 123.1612 | 41.9
LAGISZA-BLACHOWNIA | 19T110000006742A | PSE | LAGISZA | BLACHOWNIA | 220 | 645 | 587.5 | 530 | 587.5 |  |  |  | 370 | 760 | 5.2901 | 28.401 | 174.4421 | 66.1
LAGISZA-BLACHOWNIA | 19T110000006742A | PSE | LAGISZA | BLACHOWNIA | 220 | 645 | 587.5 | 530 | 587.5 |  |  |  | 370 | 760 | 5.2901 | 28.401 | 174.4421 | 66.1
KATOWICE-LAGISZA | 19T1100000067446 | PSE | KATOWICE | LAGISZA | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 0.939 | 6.8486 | 46.0744 | 16.7
KATOWICE-LAGISZA | 19T1100000067446 | PSE | KATOWICE | LAGISZA | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 0.939 | 6.8486 | 46.0744 | 16.7
SKAWINA-KLIKOWA | 19T1100000067462 | PSE | SKAWINA | KLIKOWA | 220 | 825 | 782.5 | 740 | 782.5 |  |  |  | 625 | 910 | 7.652 | 40.249 | 236.6529 | 91.8
POREBA-CZECZOT | 19T1100000067470 | PSE | POREBA | CZECZOT | 220 | 895 | 847.5 | 800 | 847.5 |  |  |  | 675 | 990 | 1.0406 | 7.168 | 51.9421 | 18.1
BLACHOWNIA-WIELOPOLE | 19T000000000482S | PSE | BLACHOWNIA | WIELOPOLE | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 2.8701 | 19.81 | 149.0702 | 50.8
JOACHIMOW-LOSNICE | 19T110000006748Z | PSE | JOACHIMOW | LOSNICE | 220 | 1005 | 947.5 | 890 | 947.5 |  |  |  | 735 | 1120 | 1.8876 | 13.779 | 92.9339 | 33.5
BYCZYNA-SKAWINA | 19T110000006440Q | PSE | BYCZYNA | SKAWINA | 220 | 825 | 782.5 | 740 | 782.5 |  |  |  | 625 | 910 | 3.9688 | 20.822 | 131.5702 | 47.7
BYCZYNA-SKAWINA | 19T110000006441O | PSE | BYCZYNA | SKAWINA | 220 | 825 | 782.5 | 740 | 782.5 |  |  |  | 625 | 910 | 3.9688 | 20.822 | 131.5702 | 47.7
BUJAKOW-BYCZYNA | 19T000000000338Z | PSE | BUJAKOW | BYCZYNA | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 2.5023 | 18.808 | 123.2851 | 44.4
BIERUN-BYCZYNA | 19T1100000064595 | PSE | BIERUN | BYCZYNA | 220 | 825 | 782.5 | 740 | 782.5 |  |  |  | 625 | 910 | 1.089 | 6.8922 | 54.2562 | 16.6
BYCZYNA-POREBA | 19T110000006460K | PSE | BYCZYNA | POREBA | 220 | 895 | 847.5 | 800 | 847.5 |  |  |  | 675 | 990 | 2.0909 | 13.6 | 101.0537 | 33.4
BIERUN-KOMOROWICE | 19T110000006749X | PSE | BIERUN | KOMOROWICE | 220 | 645 | 587.5 | 530 | 587.5 |  |  |  | 370 | 760 | 5.4305 | 34.238 | 239.0702 | 84.5
SIERSZA-LUBOCZA | 19T110000006750B | PSE | SIERSZA | LUBOCZA | 220 | 1005 | 947.5 | 890 | 947.5 |  |  |  | 735 | 1120 | 2.9088 | 20.401 | 148.5744 | 51.7
SIERSZA-LUBOCZA | 19T1100000067519 | PSE | SIERSZA | LUBOCZA | 220 | 1005 | 947.5 | 890 | 947.5 |  |  |  | 735 | 1120 | 2.9088 | 20.401 | 148.5744 | 51.7
KLIKOWA-LUBOCZA | 19T1100000067527 | PSE | KLIKOWA | LUBOCZA | 220 | 790 | 745 | 700 | 745 |  |  |  | 580 | 880 | 5.6676 | 30.4 | 182.0248 | 69.9
ANIOLOW-JOACHIMOW | 19T1100000067535 | PSE | ANIOLOW | JOACHIMOW | 220 | 705 | 642.5 | 580 | 642.5 |  |  |  | 405 | 830 | 1.0116 | 6.292 | 41.3636 | 15.1
JOACHIMOW-HUTA CZESTOCHOWA | 19T1100000067543 | PSE | JOACHIMOW | HUTA CZESTOCHOWA | 220 | 1120 | 1075 | 1030 | 1075 |  |  |  | 910 | 1210 | 0.6679 | 4.7916 | 32.7273 | 11.8
HUTA CZESTOCHOWA-WRZOSOWA | 19T1100000067551 | PSE | HUTA CZESTOCHOWA | WRZOSOWA | 220 | 995 | 942.5 | 890 | 942.5 |  |  |  | 750 | 1100 | 0.2807 | 2.0183 | 14.1322 | 5
BUJAKOW-PORABKA-ZAR | 19T110000006757Y | PSE | BUJAKOW | PORABKA-ZAR | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 0.4114 | 3.0589 | 19.2355 | 7.2
BUJAKOW-PORABKA-ZAR | 19T110000006758W | PSE | BUJAKOW | PORABKA-ZAR | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 0.4114 | 2.9621 | 19.9174 | 7.2
BUJAKOW-KOMOROWICE | 19T1100000064692 | PSE | BUJAKOW | KOMOROWICE | 220 | 1190 | 1140 | 1090 | 1140 |  |  |  | 960 | 1200 | 0.7599 | 5.4305 | 38.3058 | 13.5
KOPANINA-WIELOPOLE | 19T0000000003508 | PSE | KOPANINA | WIELOPOLE | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 1.5198 | 10.45 | 79.3182 | 27.9
MOSZCZENICA-WIELOPOLE | 19T110000006454F | PSE | MOSZCZENICA | WIELOPOLE | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 2.2022 | 15.28 | 114.2769 | 39.1
HALEMBA-KOPANINA | 19T110000006439B | PSE | HALEMBA | KOPANINA | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 0.7018 | 4.8787 | 35.5165 | 12.4
KATOWICE-KOPANINA | 19T000000006408A | PSE | KATOWICE | KOPANINA | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 1.8586 | 13.17 | 93.3264 | 32.9
CZECZOT-MOSZCZENICA | 19T110000006759U | PSE | CZECZOT | MOSZCZENICA | 220 | 705 | 642.5 | 580 | 642.5 |  |  |  | 405 | 830 | 3.7607 | 19.98 | 132.0455 | 48
BYCZYNA-JAMKI | 19T110000006461I | PSE | BYCZYNA | JAMKI | 220 | 785 | 717.5 | 650 | 717.5 |  |  |  | 460 | 920 | 1.602 | 11.601 | 90.3512 | 28.3
LOSNICE-SIERSZA | 19T1100000067608 | PSE | LOSNICE | SIERSZA | 220 | 850 | 800 | 750 | 800 |  |  |  | 615 | 950 | 2.8508 | 16.969 | 108.1612 | 40.1
KOKSOCHEMIA-LOSNICE | 19T1100000067616 | PSE | KOKSOCHEMIA | LOSNICE | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 1.5294 | 11.51 | 72.8719 | 27.2
BYCZYNA-SIERSZA | 19T110000006463E | PSE | BYCZYNA | SIERSZA | 220 | 1190 | 1140 | 1090 | 1140 |  |  |  | 960 | 1200 | 0.8809 | 6.1904 | 51.1983 | 15.7
JAMKI-LAGISZA | 19T1100000067624 | PSE | JAMKI | LAGISZA | 220 | 645 | 587.5 | 530 | 587.5 |  |  |  | 370 | 760 | 0.8276 | 4.719 | 28.7397 | 10.9
BYCZYNA-KOKSOCHEMIA | 19T110000006462G | PSE | BYCZYNA | KOKSOCHEMIA | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 1.6698 | 12.129 | 94.8554 | 29.8
BYCZYNA-SIERSZA | 19T110000006464C | PSE | BYCZYNA | SIERSZA | 220 | 1190 | 1140 | 1090 | 1140 |  |  |  | 960 | 1200 | 0.8809 | 6.2 | 52.7273 | 15.8
KEDZIERZYN-GROSZOWICE | 19T1100000067632 | PSE | KEDZIERZYN | GROSZOWICE | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 2.7588 | 20.338 | 133.6983 | 49
SKAWINA-WANDA | 19T1100000067640 | PSE | SKAWINA | WANDA | 220 | 825 | 782.5 | 740 | 782.5 |  |  |  | 625 | 910 | 2.2119 | 12.182 | 74.9587 | 28.4
LUBOCZA-WANDA | 19T110000006765Z | PSE | LUBOCZA | WANDA | 220 | 790 | 745 | 700 | 745 |  |  |  | 580 | 880 | 1.0309 | 6.4808 | 44.4215 | 15.9
MIKULOWA-POLKOWICE | 19T000000000369O | PSE | MIKULOWA | POLKOWICE | 220 | 1120 | 1075 | 1030 | 1075 |  |  |  | 910 | 1210 | 5.0288 | 43.478 | 235.9917 | 89.3
MIKULOWA-POLKOWICE | 19T0000000003702 | PSE | MIKULOWA | POLKOWICE | 220 | 1120 | 1075 | 1030 | 1075 |  |  |  | 910 | 1210 | 5.0288 | 43.478 | 235.9917 | 89.3
MIKULOWA-SWIEBODZICE | 19T0000000003710 | PSE | MIKULOWA | SWIEBODZICE | 220 | 850 | 800 | 750 | 800 |  |  |  | 615 | 950 | 7.0422 | 39.349 | 274.3595 | 97.6
MIKULOWA-SWIEBODZICE | 19T000000000372Z | PSE | MIKULOWA | SWIEBODZICE | 220 | 850 | 800 | 750 | 800 |  |  |  | 615 | 950 | 7.0422 | 39.349 | 274.3595 | 97.6
CZERWONAK-PATNOW | 19T110000006766X | PSE | CZERWONAK | PATNOW | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 5.3482 | 39.238 | 264.9587 | 95
MIKULOWA-CIEPLICE | 19T000000000378N | PSE | MIKULOWA | CIEPLICE | 220 | 1005 | 947.5 | 890 | 947.5 |  |  |  | 735 | 1120 | 2.8895 | 21.649 | 139.1529 | 51.3
POLKOWICE-PLEWISKA | 19T0000000064098 | PSE | POLKOWICE | PLEWISKA | 220 | 895 | 847.5 | 800 | 847.5 |  |  |  | 675 | 990 | 8.4022 | 53.09 | 336.1157 | 116.5
POLKOWICE-LESZNO | 19T000000006410N | PSE | POLKOWICE | LESZNO | 220 | 895 | 847.5 | 800 | 847.5 |  |  |  | 675 | 990 | 4.5399 | 29.49 | 184.5868 | 64.4
MIKULOWA-LESNIOW | 19T000000000382W | PSE | MIKULOWA | LESNIOW | 220 | 1200 | 1150 | 1100 | 1150 |  |  |  | 970 | 1220 | 6.0016 | 44.741 | 324.7727 | 107
CIEPLICE-BOGUSZOW | 19T110000006448A | PSE | CIEPLICE | BOGUSZOW | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 2.4878 | 18.518 | 122.5826 | 44.3
GORZOW-KRAJNIK | 19T000000006405G | PSE | GORZOW | KRAJNIK | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 5.1401 | 38.188 | 249.6901 | 91.3
ZUKOWICE-LESNIOW | 19T000000006411L | PSE | ZUKOWICE | LESNIOW | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 3.722 | 27.54 | 179.1942 | 66.2
PLEWISKA-POZNAN PLD | 19T110000006767V | PSE | PLEWISKA | POZNAN PLD | 220 | 645.2 | 587.6 | 530.1 | 587.6 |  |  |  | 370 | 720 | 1.1277 | 7.9521 | 48.1198 | 4.8
CZERWONAK-PLEWISKA | 19T110000006447C | PSE | CZERWONAK | PLEWISKA | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 1.7182 | 12.618 | 84.6281 | 30.56
PILA KRZEWINA-PLEWISKA | 19T000000006387T | PSE | PILA KRZEWINA | PLEWISKA | 220 | 850 | 800 | 750 | 800 |  |  |  | 615 | 950 | 2.178 | 26.702 | 367.2727 | 92.37
LESZNO-PLEWISKA | 19T0000000064195 | PSE | LESZNO | PLEWISKA | 220 | 895 | 847.5 | 800 | 847.5 |  |  |  | 675 | 990 | 4.5206 | 26.088 | 179.4008 | 64
ADAMOW-KONIN | 19T110000006768T | PSE | ADAMOW | KONIN | 220 | 935 | 897.5 | 860 | 897.5 |  |  |  | 760 | 1010 | 3.3783 | 18.102 | 112.8719 | 42
ADAMOW-KONIN | 19T110000006769R | PSE | ADAMOW | KONIN | 220 | 1200 | 1150 | 1100 | 1150 |  |  |  | 970 | 1250 | 2.1102 | 15.498 | 103.9256 | 37.5
KONIN-PATNOW | 19T1100000067705 | PSE | KONIN | PATNOW | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 0.2904 | 1.6988 | 11.4669 | 4.1
KONIN-PATNOW | 19T1100000067713 | PSE | KONIN | PATNOW | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 0.2904 | 1.6988 | 11.4669 | 4.1
GORZOW-LESNIOW | 19T000000006413H | PSE | GORZOW | LESNIOW | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 5.1207 | 37.568 | 252.1281 | 91
KRAJNIK-MORZYCZYN | 19T000000006404I | PSE | KRAJNIK | MORZYCZYN | 220 | 1005 | 947.5 | 890 | 947.5 |  |  |  | 735 | 1120 | 2.27 | 16.872 | 110.2893 | 40.3
GLINKI-KRAJNIK | 19T000000006406E | PSE | GLINKI | KRAJNIK | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 2.7491 | 19.418 | 145.3099 | 48.8
GLINKI-POLICE | 19T1100000067721 | PSE | GLINKI | POLICE | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 0.5082 | 3.5477 | 25.9917 | 9
MORZYCZYN-POLICE | 19T110000006453H | PSE | MORZYCZYN | POLICE | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 3.5719 | 26.339 | 245.0413 | 64.1
MORZYCZYN-RECLAW | 19T110000006774Y | PSE | MORZYCZYN | RECLAW | 220 | 830 | 755 | 680 | 755 |  |  |  | 380 | 980 | 4.1237 | 30.661 | 214.6281 | 0
RECLAW-GLINKI | 19T110000006775W | PSE | RECLAW | GLINKI | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 2.6572 | 19.742 | 138.1818 | 47.482
BOGUSZOW-SWIEBODZICE | 19T1100000064498 | PSE | BOGUSZOW | SWIEBODZICE | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 1.0696 | 7.8311 | 52.5 | 19
SWIEBODZICE-ZABKOWICE | 19T000000000315A | PSE | SWIEBODZICE | ZABKOWICE | 220 | 830 | 755 | 680 | 755 |  |  |  | 475 | 980 | 2.512 | 18.76 | 179.5041 | 45.3
POLKOWICE-ZUKOWICE | 19T000000006414F | PSE | POLKOWICE | ZUKOWICE | 220 | 1000 | 1000 | 950.3 | 1000 |  |  |  | 805 | 1000 | 1.1422 | 8.4506 | 55.2893 | 20.1
WLOCLAWEK AZ-OLSZTYN | 19T110000006776U | PSE | WLOCLAWEK AZ | OLSZTYN | 220 | 705 | 642.5 | 580 | 642.5 |  |  |  | 405 | 720 | 13.112 | 77.401 | 539.7727 | 181.9
JASINIEC-GRUDZIADZ | 19T110000006777S | PSE | JASINIEC | GRUDZIADZ | 220 | 720 | 720 | 679.6 | 720 |  |  |  | 475 | 720 | 2.2796 | 21.93 | 270.2479 | 73.7
ZYDOWO KIERZKOWO-GDANSK | 19T000000006402M | PSE | ZYDOWO KIERZKOWO | GDANSK | 220 | 705 | 642.5 | 580 | 642.5 |  |  |  | 405 | 720 | 4.5883 | 39.78 | 455.8264 | 127.7
BYDGOSZCZ ZA-JASINIEC | 19T110000006778Q | PSE | BYDGOSZCZ ZA | JASINIEC | 220 | 720 | 720 | 679.6 | 720 |  |  |  | 475 | 720 | 0.8809 | 10.072 | 109.8554 | 31.725
WLOCLAWEK AZ-TORUN ELANA | 19T110000006779O | PSE | WLOCLAWEK AZ | TORUN ELANA | 220 | 720 | 720 | 679.6 | 720 |  |  |  | 475 | 720 | 3.5719 | 26.552 | 192.5207 | 63.5
TORUN ELANA-GRUDZIADZ | 19T1100000067802 | PSE | TORUN ELANA | GRUDZIADZ | 220 | 720 | 720 | 679.6 | 720 |  |  |  | 475 | 720 | 2.691 | 20.318 | 127.2314 | 47.8
ZYDOWO-ZYDOWO KIERZKOWO | 19T000000006403K | PSE | ZYDOWO | ZYDOWO KIERZKOWO | 220 | 720 | 720 | 720 | 720 |  |  |  | 720 | 720 | 0.1888 | 1.0212 | 6.7562 | 2.5
OLSZTYN MATKI-OLSZTYN | 19T1100000067810 | PSE | OLSZTYN MATKI | OLSZTYN | 220 | 1190 | 1140 | 1090 | 1140 |  |  |  | 960 | 1200 | 0.3678 | 3.7704 | 51.7769 | 14.2
DUNOWO-ZYDOWO | 19T0000000064276 | PSE | DUNOWO | ZYDOWO | 220 | 960 | 947.4 | 889.9 | 947.4 |  |  |  | 735 | 960 | 2.7491 | 20.401 | 147.9339 | 48.8
T HAL-BYĆ-BYCZYNA | 19T110000006782Z | PSE | T HAL-BYĆ | BYCZYNA | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 0.9293 | 6.5292 | 58.843 | 16.6
HALEMBA-T HAL-BYĆ | 19T110000006783X | PSE | HALEMBA | T HAL-BYĆ | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 1.1519 | 8.0683 | 58.8017 | 20.4
T HAL-BYĆ-LAGISZA | 19T110000006784V | PSE | T HAL-BYĆ | LAGISZA | 220 | 1060 | 1005 | 950 | 1005 |  |  |  | 805 | 1170 | 1.3504 | 9.7623 | 66.1983 | 23.9
WRZOSOWA-T JOA-LAG | 19T110000006785T | PSE | WRZOSOWA | T JOA-LAG | 220 | 1190 | 1140 | 1090 | 1140 |  |  |  | 750 | 1100 | 0.3194 | 2.4297 | 15.2893 | 5.7
T JOA-LAG-LAGISZA | 19T110000006786R | PSE | T JOA-LAG | LAGISZA | 220 | 1120 | 1075 | 1030 | 1075 |  |  |  | 750 | 1100 | 2.5991 | 19.912 | 120.8264 | 46.1
T JOA-LAG-JOACHIMOW | 19T110000006787P | PSE | T JOA-LAG | JOACHIMOW | 220 | 1120 | 1075 | 1030 | 1075 |  |  |  | 580 | 880 | 0.36 | 2.5797 | 17.5 | 6.3
PLOCK-ROGOWIEC | 19T000000001285P | PSE | PLOCK | ROGOWIEC | 400 | 2000 | 1894.4 | 1779.6 | 1894.4 |  |  |  | 1470 | 2000 | 5.728 | 66.624 | 711.7625 | 203.7
MILOSNA-OLTARZEW | 19T000000006393Y | PSE | MILOSNA | OLTARZEW | 400 | 1200 | 1200 | 1200 | 1200 |  |  |  | 950 | 1200 | 2.112 | 24.48 | 265.0375 | 75.3
OLTARZEW-PLOCK | 19T110000006788N | PSE | OLTARZEW | PLOCK | 400 | 1660 | 1510 | 1360 | 1510 |  |  |  | 950 | 1960 | 2.688 | 31.536 | 329.1812 | 95.3
OLTARZEW-MOSCISKA | 19T000000006394W | PSE | OLTARZEW | MOSCISKA | 400 | 1660 | 1510 | 1360 | 1510 |  |  |  | 950 | 1960 | 0.384 | 4.544 | 49.1187 | 14
ROGOWIEC-OLTARZEW | 19T110000006789L | PSE | ROGOWIEC | OLTARZEW | 400 | 2000 | 1894.4 | 1779.6 | 1894.4 |  |  |  | 1470 | 2000 | 5.072 | 58.88 | 630.5813 | 180.2
LOMZA SYSTEMOWA-OSTROLEKA | 19T000000001293Q | PSE | LOMZA SYSTEMOWA | OSTROLEKA | 400 | 2760 | 2655 | 2550 | 2655 |  |  |  | 2280 | 2970 | 1.04 | 11.184 | 142.4375 | 37.3
LOMZA SYSTEMOWA-OSTROLEKA | 19T000000001294O | PSE | LOMZA SYSTEMOWA | OSTROLEKA | 400 | 2760 | 2655 | 2550 | 2655 |  |  |  | 2280 | 2970 | 1.04 | 11.184 | 142.4375 | 37.3
SIEDLCE UJRZANOW-NAREW | 19T000000006425A | PSE | SIEDLCE UJRZANOW | NAREW | 400 | 1200 | 1200 | 1200 | 1200 |  |  |  | 950 | 1200 | 5.296 | 61.072 | 684.5812 | 190.9
MOSCISKA-MILOSNA | 19T110000006791Y | PSE | MOSCISKA | MILOSNA | 400 | 1660 | 1510 | 1360 | 1510 |  |  |  | 950 | 1960 | 1.76 | 20.336 | 220.0375 | 62.6
STANISLAWOW-MILOSNA | 19T0000000063814 | PSE | STANISLAWOW | MILOSNA | 400 | 2000 | 2000 | 2000 | 2000 |  |  |  | 950 | 1960 | 0.56 | 6.416 | 69.9375 | 19.8
STANISLAWOW-MILOSNA | 19T0000000063822 | PSE | STANISLAWOW | MILOSNA | 400 | 1200 | 1200 | 1200 | 1200 |  |  |  | 1200 | 1200 | 0.56 | 6.48 | 69.8375 | 19.9
SIEDLCE UJRZANOW-STANISLAWOW | 19T0000000064268 | PSE | SIEDLCE UJRZANOW | STANISLAWOW | 400 | 1660 | 1510 | 1360 | 1510 |  |  |  | 950 | 1960 | 2.832 | 33.072 | 418.1812 | 109.6
ROGOWIEC-TREBACZEW | 19T110000006792W | PSE | ROGOWIEC | TREBACZEW | 400 | 2000 | 2000 | 2000 | 2000 |  |  |  | 1840 | 2000 | 1.216 | 13.904 | 150.5625 | 42.8
LOMZA SYSTEMOWA-ELK BIS | 19T0000000063741 | PSE | LOMZA SYSTEMOWA | ELK BIS | 400 | 2760 | 2655 | 2550 | 2655 |  |  |  | 2280 | 2970 | 2.336 | 24.672 | 323.1813 | 83.3
LOMZA SYSTEMOWA-ELK BIS | 19T000000006376Y | PSE | LOMZA SYSTEMOWA | ELK BIS | 400 | 2760 | 2655 | 2550 | 2655 |  |  |  | 2280 | 2970 | 2.336 | 24.688 | 323.3813 | 83.4
LOMZA SYSTEMOWA-NAREW | 19T000000001299E | PSE | LOMZA SYSTEMOWA | NAREW | 400 | 1500 | 1500 | 1500 | 1500 |  |  |  | 1500 | 1500 | 2.24 | 24.256 | 303 | 80
KOZIENICE-LUBLIN | 19T110000006793U | PSE | KOZIENICE | LUBLIN | 400 | 1000 | 1000 | 1000 | 1000 |  |  |  | 950.5 | 1000 | 2.72 | 31.632 | 333.6625 | 96.5
OSTROWIEC-POLANIEC | 19T110000006794S | PSE | OSTROWIEC | POLANIEC | 400 | 1660 | 1510 | 1360 | 1510 |  |  |  | 950 | 1960 | 1.856 | 20.8 | 211.6 | 62.2
POLANIEC-KIELCE | 19T110000006795Q | PSE | POLANIEC | KIELCE | 400 | 1660 | 1510 | 1360 | 1510 |  |  |  | 950 | 1960 | 3.488 | 40.576 | 428.6188 | 124
POLANIEC-RZESZOW | 19T000000006420K | PSE | POLANIEC | RZESZOW | 400 | 1990 | 1865 | 1740 | 1865 |  |  |  | 1410 | 2000 | 1.68 | 17.968 | 176.2188 | 52.6
RZESZOW-KROSNO ISKRZYNIA | 19T000000001304A | PSE | RZESZOW | KROSNO ISKRZYNIA | 400 | 1660 | 1510 | 1360 | 1510 |  |  |  | 950 | 1960 | 1.904 | 22.848 | 229.1625 | 67.7
KOZIENICE-OSTROWIEC | 19T110000006796O | PSE | KOZIENICE | OSTROWIEC | 400 | 1660 | 1510 | 1360 | 1510 |  |  |  | 950 | 1960 | 2.944 | 34.224 | 361.0625 | 104.5
WIELOPOLE-JOACHIMOW | 19T000000006388R | PSE | WIELOPOLE | JOACHIMOW | 400 | 2000 | 2000 | 1900.7 | 2000 |  |  |  | 1610 | 2000 | 3.856 | 44.512 | 481.7 | 137
WIELOPOLE-DOBRZEN | 19T0000000064284 | PSE | WIELOPOLE | DOBRZEN | 400 | 2000 | 2000 | 1900.7 | 2000 |  |  |  | 1610 | 2000 | 3.408 | 38.912 | 423.4 | 120.9
ROKITNICA-LAGISZA | 19T110000006444I | PSE | ROKITNICA | LAGISZA | 400 | 2000 | 2000 | 1900.7 | 2000 |  |  |  | 1610 | 2000 | 1.184 | 13.328 | 150.2188 | 41.8
SKAWINA-BYCZYNA | 19T000000006397Q | PSE | SKAWINA | BYCZYNA | 400 | 1660 | 1510 | 1360 | 1510 |  |  |  | 950 | 1960 | 1.568 | 18.048 | 197.5813 | 55.8
SKAWINA-TUCZNAWA | 19T000000006398O | PSE | SKAWINA | TUCZNAWA | 400 | 1660 | 1510 | 1360 | 1510 |  |  |  | 950 | 1960 | 2.384 | 27.472 | 298.2 | 84.6
TARNOW-SKAWINA | 19T000000006399M | PSE | TARNOW | SKAWINA | 400 | 1660 | 1510 | 1360 | 1510 |  |  |  | 950 | 1960 | 2.784 | 32.144 | 350.2812 | 99.2
WIELOPOLE-ROKITNICA | 19T000000006407C | PSE | WIELOPOLE | ROKITNICA | 400 | 2000 | 2000 | 1900.7 | 2000 |  |  |  | 1610 | 2000 | 1.472 | 16.992 | 183.7812 | 52.3
LAGISZA-TUCZNAWA | 19T0000000013139 | PSE | LAGISZA | TUCZNAWA | 400 | 2000 | 2000 | 1900.7 | 2000 |  |  |  | 1610 | 2000 | 0.704 | 7.856 | 91.0375 | 25
BYCZYNA-TUCZNAWA | 19T000000006389P | PSE | BYCZYNA | TUCZNAWA | 400 | 1200 | 1200 | 1200 | 1200 |  |  |  | 950 | 1200 | 0.816 | 9.584 | 102.2 | 29.3
CZARNA-MIKULOWA | 19T0000000013147 | PSE | CZARNA | MIKULOWA | 400 | 2380 | 2280 | 2180 | 2280 |  |  |  | 1920 | 2580 | 3.264 | 39.552 | 507.7375 | 132.1
CZARNA-PASIKUROWICE | 19T0000000013155 | PSE | CZARNA | PASIKUROWICE | 400 | 2380 | 2280 | 2180 | 2280 |  |  |  | 1920 | 2400 | 2.736 | 28.14 | 284.1 | 83.4
PATNOW-KROMOLICE | 19T110000006797M | PSE | PATNOW | KROMOLICE | 400 | 2444 | 2316.8 | 2189.5 | 2316.8 |  |  |  | 1845 | 2500 | 2.208 | 23.536 | 308.4812 | 79.395
KROMOLICE-OSTROW WLKP | 19T0000000013171 | PSE | KROMOLICE | OSTROW WLKP | 400 | 1800 | 1800 | 1800 | 1800 |  |  |  | 1800 | 1800 | 3.136 | 32.816 | 443.0375 | 112.5
PASIKUROWICE-OSTROW WLKP | 19T000000006421I | PSE | PASIKUROWICE | OSTROW WLKP | 400 | 2000 | 2000 | 1900.7 | 2000 |  |  |  | 1610 | 2000 | 2.176 | 25.584 | 262.2812 | 77
SWIEBODZICE-WROCLAW | 19T000000001320C | PSE | SWIEBODZICE | WROCLAW | 400 | 1200 | 1200 | 1200 | 1200 |  |  |  | 1200 | 1200 | 1.2 | 12.496 | 168.8375 | 43.3
MIKULOWA-PASIKUROWICE | 19T110000006437F | PSE | MIKULOWA | PASIKUROWICE | 400 | 2400 | 2400 | 2400 | 2400 |  |  |  | 2000 | 2000 | 3.568 | 43.584 | 599.9 | 150.9
PATNOW-KROMOLICE | 19T110000006798K | PSE | PATNOW | KROMOLICE | 400 | 2444 | 2316.8 | 2189.5 | 2316.8 |  |  |  | 1845 | 2500 | 2.208 | 23.536 | 308.4812 | 79.545
KROMOLICE-PLEWISKA | 19T0000000013228 | PSE | KROMOLICE | PLEWISKA | 400 | 2000 | 2000 | 2000 | 2000 |  |  |  | 1845 | 2000 | 0.864 | 8.992 | 121.4188 | 30.8
KROMOLICE-PLEWISKA | 19T000000006415D | PSE | KROMOLICE | PLEWISKA | 400 | 2445 | 2317.5 | 2190 | 2317.5 |  |  |  | 1845 | 2700 | 0.864 | 8.992 | 121.4188 | 30.8
KRAJNIK-MORZYCZYN | 19T0000000013236 | PSE | KRAJNIK | MORZYCZYN | 400 | 2120 | 2010 | 1900 | 2010 |  |  |  | 1470 | 2240 | 1.168 | 13.744 | 143.2625 | 41.5
CZARNA-POLKOWICE | 19T000000006416B | PSE | CZARNA | POLKOWICE | 400 | 2400 | 2400 | 2400 | 2400 |  |  |  | 2280 | 2400 | 0.656 | 6.928 | 90.7625 | 23.4
CZARNA-POLKOWICE | 19T0000000064179 | PSE | CZARNA | POLKOWICE | 400 | 2400 | 2400 | 2400 | 2400 |  |  |  | 2280 | 2400 | 0.656 | 6.928 | 90.7188 | 23.4
KRAJNIK-PLEWISKA | 19T0000000013244 | PSE | KRAJNIK | PLEWISKA | 400 | 2000 | 2000 | 1900.7 | 2000 |  |  |  | 1610 | 2000 | 5.968 | 69.504 | 732.5 | 212
DUNOWO-SLUPSK | 19T0000000013252 | PSE | DUNOWO | SLUPSK | 400 | 1500 | 1500 | 1359.3 | 1500 |  |  |  | 950 | 1500 | 2.096 | 24.768 | 257.2 | 73.1
GRUDZIADZ-GDANSK-BLONI | 19T0000000013260 | PSE | GRUDZIADZ | GDANSK-BLONI | 400 | 1200 | 1200 | 1200 | 1200 |  |  |  | 1200 | 1200 | 3.584 | 41.696 | 439.4 | 127.2
GDANSK-BLONI-OLSZTYN-MATK | 19T000000006395U | PSE | GDANSK-BLONI | OLSZTYN-MATK | 400 | 1200 | 1200 | 1200 | 1200 |  |  |  | 950 | 1200 | 3.84 | 44.72 | 471.3 | 136.4
SLUPSK-ZARNOWIEC | 19T000000001328X | PSE | SLUPSK | ZARNOWIEC | 400 | 1500 | 1500 | 1359.3 | 1500 |  |  |  | 950 | 1500 | 2.4 | 28.288 | 293.4 | 87.5
JASINIEC-GRUDZIADZ | 19T110000006799I | PSE | JASINIEC | GRUDZIADZ | 400 | 2250 | 2250 | 2250 | 2250 |  |  |  | 2250 | 2250 | 2.112 | 21.344 | 303.6375 | 73.7
PELPLIN-GRUDZIADZ | 19T110000006465A | PSE | PELPLIN | GRUDZIADZ | 400 | 3000 | 2970.1 | 2855.1 | 2970.1 |  |  |  | 2560 | 3000 | 1.6 | 19.952 | 284.1187 | 75
PELPLIN-GRUDZIADZ | 19T1100000064668 | PSE | PELPLIN | GRUDZIADZ | 400 | 3000 | 2970.1 | 2855.1 | 2970.1 |  |  |  | 2560 | 3000 | 1.6 | 19.856 | 282.4187 | 75
GDANSK PRZYJAZN-ZYDOWO KIERZKOWO | 19T110000006432P | PSE | GDANSK PRZYJAZN | ZYDOWO KIERZKOWO | 400 | 2760 | 2655 | 2550 | 2655 |  |  |  | 2280 | 2970 | 3.264 | 33.424 | 456.6375 | 120.2
ZYDOWO KIERZKOWO-SLUPSK | 19T110000006434L | PSE | ZYDOWO KIERZKOWO | SLUPSK | 400 | 1500 | 1500 | 1500 | 1500 |  |  |  | 1500 | 1500 | 1.424 | 16.928 | 245.5625 | 60.8
ZYDOWO KIERZKOWO-SLUPSK | 19T110000006435J | PSE | ZYDOWO KIERZKOWO | SLUPSK | 400 | 1500 | 1500 | 1500 | 1500 |  |  |  | 1500 | 1500 | 1.424 | 16.896 | 254.4187 | 60.8
ZARNOWIEC-GDANSK | 19T0000000013317 | PSE | ZARNOWIEC | GDANSK | 400 | 1200 | 1200 | 1200 | 1200 |  |  |  | 950 | 1200 | 1.52 | 17.584 | 190.4375 | 54.1
GDANSK-GDANSK-BLONI | 19T0000000013325 | PSE | GDANSK | GDANSK-BLONI | 400 | 1200 | 1200 | 1200 | 1200 |  |  |  | 950 | 1200 | 0.688 | 7.872 | 85.3813 | 24.3
GDANSK PRZYJAZN-GDANSK-BLONI | 19T110000006430T | PSE | GDANSK PRZYJAZN | GDANSK-BLONI | 400 | 1200 | 1200 | 1200 | 1200 |  |  |  | 950 | 1200 | 0.688 | 8.528 | 112 | 28.9
ZARNOWIEC-GDANSK PRZYJAZN | 19T110000006431R | PSE | ZARNOWIEC | GDANSK PRZYJAZN | 400 | 1200 | 1200 | 1200 | 1200 |  |  |  | 950 | 1200 | 1.392 | 17.568 | 230.8375 | 59.4
GDANSK PRZYJAZN-PELPLIN | 19T1100000064676 | PSE | GDANSK PRZYJAZN | PELPLIN | 400 | 3000 | 2970.1 | 2855.1 | 2970.1 |  |  |  | 2560 | 3000 | 1.024 | 12.928 | 192.0625 | 44
GDANSK PRZYJAZN-PELPLIN | 19T1100000064684 | PSE | GDANSK PRZYJAZN | PELPLIN | 400 | 3000 | 2970.1 | 2855.1 | 2970.1 |  |  |  | 2560 | 3000 | 1.008 | 12.88 | 192.0188 | 44
LIT 400kV N0 1 AGASSES (LES) - JONQUIERES | 17T0000000151385 | RTE | AGASSES (LES) | JONQUIERES | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.206 | 2.707 | 44.844 | 10.281
LIT 400kV N0 1 AGASSES (LES) - TAVEL | 17T0000000151393 | RTE | AGASSES (LES) | TAVEL | 400 | 2462 | 2644 | 2644 | 2798 | [5 empty] | 0.46 | 4.671 | 57.672 | 15.596
LIT 400kV N0 1 ALBERTVILLE - COCHE (LA) | 17T-FR-00000044Z | RTE | ALBERTVILLE | COCHE (LA) | 400 | 2585 | 2633 | 2633 | 2715 | [5 empty] | 0.694 | 9.818 | 63.864 | 22.583
LIT 400kV N0 1 ALBERTVILLE - GRANDE-ILE | 17T-FR-00000057Q | RTE | ALBERTVILLE | GRANDE-ILE | 400 | 3099 | 3441 | 3441 | 3741 | [5 empty] | 0.739 | 11.29 | 169.156 | 40.744
LIT 400kV N0 1 ALBERTVILLE-MONTAGNY-LES-LANCHES | 17T-FR-00000047T | RTE | ALBERTVILLE | MONTAGNY-LES-LANCHES | 400 | 2170 | 2318 | 2318 | 2498 | [5 empty] | 1.265 | 12.616 | 139.45 | 37.517
LIT 400kV N0 1 ARGIA (BAYONNE SUD) - CANTEGRIT | 17T-FR-00000037W | RTE | ARGIA (BAYONNE SUD) | CANTEGRIT | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 2.608 | 29.184 | 280.504 | 83.807
LIT 400kV N0 1 ARGOEUVES - CHEVALET | 17T000000015954C | RTE | ARGOEUVES | CHEVALET | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.842 | 11.054 | 183.034 | 41.972
LIT 400kV N0 1 ARGOEUVES - FRUGES | 17T000000015955A | RTE | ARGOEUVES | FRUGES | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.307 | 17.156 | 284.082 | 65.137
LIT 400kV N0 1 ARGOEUVES - LIMEUX | 17T0000000159568 | RTE | ARGOEUVES | LIMEUX | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.492 | 8.333 | 145.64 | 33.285
LIT 400kV N0 1 ARGOEUVES - MANDARINS | 17T0000000159576 | RTE | ARGOEUVES | MANDARINS | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 2.377 | 31.238 | 517.966 | 118.964
LIT 400kV N0 1 ARGOEUVES - PENLY (POSTE EVACUATION) | 17T0000000159592 | RTE | ARGOEUVES | PENLY (POSTE EVACUATION) | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.213 | 20.654 | 360.332 | 80.72
LIT 400kV N0 1 ARGOEUVES - TERRIER | 17T000000015960H | RTE | ARGOEUVES | TERRIER | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.684 | 22.111 | 366.272 | 83.97
LIT 400kV N0 1 AVELIN - GAVRELLE | 17T-FR-00000002E | RTE | AVELIN | GAVRELLE | 400 | 2238 | 2412 | 2412 | 2622 | [5 empty] | 0.448 | 7.862 | 136,202‬ | 30.591
LIT 400kV N0 1 AVELIN - MASTAING | 17T-FR-00000055U | RTE | AVELIN | MASTAING | 400 | 2570 | 2718 | 2718 | 2912 | [5 empty] | 0.91 | 10.249 | 111.272 | 31.358
LIT 400kV N0 1 AVELIN - WEPPES | 17T-FR-00000004A | RTE | AVELIN | WEPPES | 400 | 3078 | 3266 | 3266 | 3458 | [5 empty] | 0.532 | 6.714 | 120.67 | 21.668
LIT 400kV N0 1 AVOINE (POSTE 400 kV) - DISTRE | 17T000000016632T | RTE | AVOINE (POSTE 400 KV) | DISTRE | 400 | 3196 | 3488 | 3488 | 3582 | [5 empty] | 0.511 | 6.623 | 81.722 | 21.655
LIT 400kV N0 1 AVOINE (POSTE 400 kV) - GRILLE-AVOINE | 17T000000016633R | RTE | AVOINE (POSTE 400 KV) | GRILLE-AVOINE | 400 | 1950 | 2025 | 2025 | 2100 | [5 empty] | 0.009 | 0.149 | 1.094 | 0.375
LIT 400kV N0 1 AVOINE (POSTE 400 kV) - LARCAY | 17T000000016634P | RTE | AVOINE (POSTE 400 KV) | LARCAY | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.009 | 13.254 | 219.818 | 50.356
LIT 400kV N0 1 BAIXAS - GAUDIERE (LA) | 17T-FR-00000038U | RTE | BAIXAS | GAUDIERE (LA) | 400 | 4400 | 4500 | 4500 | 4500 | [5 empty] | 1.565 | 22.203 | 263.746 | 71.084
LIT 400kV N0 1 BARNABOS - PENLY (POSTE EVACUATION) | 17T000000017229T | RTE | BARNABOS | PENLY (POSTE EVACUATION) | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.707 | 12.046 | 210.27 | 47.082
LIT 400kV N0 1 BARNABOS - ROUGEMONTIER | 17T0000000172315 | RTE | BARNABOS | ROUGEMONTIER | 400 | 3416 | 3622 | 3622 | 3780 | [5 empty] | 1.057 | 15.342 | 191.064 | 50.281
LIT 400kV N0 1 BARNABOS - TERRIER | 17T0000000172323 | RTE | BARNABOS | TERRIER | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 2.136 | 28.087 | 466.346 | 106.793
LIT 400kV N0 1 BARNABOS - VAUPALIERE (LA) | 17T0000000172331 | RTE | BARNABOS | VAUPALIERE (LA) | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.437 | 5.743 | 95.084 | 21.836
LIT 400kV N0 1 BARNABOS-REMISE | 17T0000000172307 | RTE | BARNABOS | REMISE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.725 | 22.672 | 374.954 | 86.154
LIT 400kV N0 1 BAYET - GREPILLES | 17T0000000173978 | RTE | BAYET | GREPILLES | 400 | 2130 | 2374 | 2374 | 2576 | [5 empty] | 2.126 | 21.558 | 266.886 | 70.752
LIT 400kV N0 1 BAYET - MARMAGNE | 17T0000000173986 | RTE | BAYET | MARMAGNE | 400 | 2130 | 2300 | 2300 | 2400 | [5 empty] | 3.707 | 37.569 | 465.896 | 123.205
LIT 400kV N0 1 BAYET - RULHAT | 17T0000000173994 | RTE | BAYET | RULHAT | 400 | 2600 | 2700 | 2700 | 2800 | [5 empty] | 1.039 | 13.658 | 226.736 | 52.395
LIT 400kV N0 1 BAYET-GAUGLIN | 17T000000017396A | RTE | BAYET | GAUGLIN | 400 | 2800 | 3000 | 3000 | 3100 | [5 empty] | 3.096 | 40.844 | 680.972 | 156.345
LIT 400kV N0 1 BEZAUMONT - HOUDREVILLE | 17T-FR-000000066 | RTE | BEZAUMONT | HOUDREVILLE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.038 | 13.645 | 226.24 | 51.843
LIT 400kV N0 1 BEZAUMONT - MARLENHEIM | 17T000000017794Z | RTE | BEZAUMONT | MARLENHEIM | 400 | 2070 | 2282 | 2282 | 2400 | [5 empty] | 4.629 | 51.059 | 625.098 | 166.234
LIT 400kV N0 1 BEZAUMONT - VIGY | 17T-FR-000000074 | RTE | BEZAUMONT | VIGY | 400 | 3294 | 3622 | 3622 | 3780 | [5 empty] | 0.886 | 11.633 | 192.46 | 44.148
LIT 400kV N0 1 BIANCON - TRANS | 17T000000017834C | RTE | BIANCON | TRANS | 400 | 2128 | 2326 | 2326 | 2482 | [5 empty] | 0.936 | 9.487 | 117.652 | 31.208
LIT 400kV N0 1 BOCTOIS - MERY-SUR-SEINE | 17T000000018037X | RTE | BOCTOIS | MERY-SUR-SEINE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.714 | 9.372 | 154.654 | 35.548
LIT 400kV N0 1 BOCTOIS - MORBRAS | 17T000000018038V | RTE | BOCTOIS | MORBRAS | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.565 | 20.572 | 341.292 | 78.18
LIT 400kV N0 1 BOISSE (LA) - CHAFFARD (LE) | 17T000000018119V | RTE | BOISSE (LA) | CHAFFARD (LE) | 400 | 1752 | 1998 | 1998 | 2172 | [5 empty] | 0.724 | 7.901 | 79.792 | 23.479
LIT 400kV N0 1 BOISSE (LA) - MIONS | 17T0000000181209 | RTE | BOISSE (LA) | MIONS | 400 | 2300 | 2450 | 2450 | 2600 | [5 empty] | 0.617 | 6.605 | 69.378 | 20.08
LIT 400kV N0 1 BOIS-TOLLOT - GENISSIAT-POSTE | 17T-FR-000000503 | RTE | BOIS-TOLLOT | GENISSIAT-POSTE | 400 | 1948 | 2162 | 2162 | 2348 | [5 empty] | 1.107 | 10.877 | 119.95 | 33.634
LIT 400kV N0 1 BOUTRE - PLAN-D ORGON | 17T000000018432R | RTE | BOUTRE | PLAN-D ORGON | 400 | 3192 | 3489 | 3489 | 3723 | [5 empty] | 1.659 | 21.818 | 362.202 | 83.165
LIT 400kV N0 1 BOUTRE - PRIONNET | 17T000000018433P | RTE | BOUTRE | PRIONNET | 400 | 3192 | 3489 | 3489 | 3723 | [5 empty] | 0.147 | 2.356 | 34.136 | 8.951
LIT 400kV N0 1 BRAUD - MARQUIS (LE) | 17T000000018481E | RTE | BRAUD | MARQUIS (LE) | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.921 | 11.921 | 147.052 | 39.424
LIT 400kV N0 1 BRAUD - PREGUILLAC | 17T000000018502W | RTE | BRAUD | PREGUILLAC | 400 | 3072 | 3414 | 3414 | 3598 | [5 empty] | 0.994 | 14.43 | 179.718 | 47.291
LIT 400kV N0 1 BREUIL (LE) - MARMAGNE | 17T0000000185909 | RTE | BREUIL (LE) | MARMAGNE | 400 | 1410 | 1632 | 1632 | 1806 | [5 empty] | 9.503 | 71.427 | 701.638 | 209.476
LIT 400kV N0 1 BREUIL (LE) - RUEYRES | 17T0000000185917 | RTE | BREUIL (LE) | RUEYRES | 400 | 1186 | 1644 | 1644 | 1968 | [5 empty] | 1.964 | 21.402 | 230.292 | 65.65
LIT 400kV N0 1 BROC-CARROS (LE) - BIANCON | 17T0000000167587 | RTE | BROC-CARROS (LE) | BIANCON | 400 | 2006 | 2192 | 2192 | 2336 | [5 empty] | 1.665 | 15.592 | 195.998 | 51.487
LIT 400kV N0 1 CALAN - CORDEMAIS-POSTE | 17T000000019480B | RTE | CALAN | CORDEMAIS-POSTE | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 4.186 | 42.432 | 525.836 | 139.524
LIT 400kV N0 1 CALAN - MARTYRE (LA) | 17T0000000194819 | RTE | CALAN | MARTYRE (LA) | 400 | 2862 | 2920 | 2920 | 3020 | [5 empty] | 2.953 | 29.941 | 370.826 | 98.335
LIT 400kV N0 1 CAPELLE (LA) - LONNY | 17T-FR-00000010F | RTE | CAPELLE (LA) | LONNY | 400 | 2196 | 2422 | 2422 | 2596 | [5 empty] | 1.639 | 17.552 | 184.352 | 53.016
LIT 400kV N0 1 CAPELLE (LA) - MASTAING | 17T-FR-00000011D | RTE | CAPELLE (LA) | MASTAING | 400 | 2570 | 2718 | 2718 | 2914 | [5 empty] | 1.887 | 20.213 | 212.312 | 60.871
LIT 400kV N0 1 CAZARIL - MARSILLON | 17T000000020569Y | RTE | CAZARIL | MARSILLON | 400 | 3316 | 3622 | 3622 | 3780 | [5 empty] | 2.096 | 29.202 | 466.798 | 101.257
LIT 400kV N0 1 CAZARIL - VERFEIL | 17T000000019790X | RTE | CAZARIL | VERFEIL | 400 | 3255 | 3600 | 3600 | 3780 | [5 empty] | 2.421 | 32.079 | 528.09 | 121.353
LIT 400kV N0 1 CERGY-MEZEROLLES | 17T000000019866Q | RTE | CERGY | MEZEROLLES | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.991 | 10.236 | 120.684 | 32.739
LIT 400kV N0 1 CERGY-TERRIER | 17T000000019867O | RTE | CERGY | TERRIER | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 0.876 | 9.212 | 102.588 | 28.595
LIT 400kV N0 1 CHAFFARD (LE) - CHAMPAGNIER | 17T0000000199989 | RTE | CHAFFARD (LE) | CHAMPAGNIER | 400 | 2110 | 2246 | 2246 | 2382 | [5 empty] | 3.161 | 35.012 | 362.502 | 104.135
LIT 400kV N0 1 CHAFFARD (LE) - COULANGE | 17T000000019997B | RTE | CHAFFARD (LE) | COULANGE | 400 | 3465 | 3544 | 3544 | 3575 | [5 empty] | 4.154 | 41.629 | 519.052 | 0
LIT 400kV N0 1 CHAFFARD (LE) - GRANDE-ILE | 17T0000000199997 | RTE | CHAFFARD (LE) | GRANDE-ILE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.44 | 20.469 | 321.628 | 76.242
LIT 400kV N0 1 CHAFFARD (LE) - MIONS | 17T000000020000G | RTE | CHAFFARD (LE) | MIONS | 400 | 1764 | 1876 | 1876 | 1988 | [5 empty] | 0.543 | 4.174 | 41.2 | 12.222
LIT 400kV N0 1 CHAFFARD (LE) - PIVOZ-CORDIER | 17T000000020001E | RTE | CHAFFARD (LE) | PIVOZ-CORDIER | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.293 | 14.857 | 170.62 | 47.327
LIT 400kV N0 1 CHAFFARD (LE) - ST-VULBAS-OUEST | 17T0000000200226 | RTE | CHAFFARD (LE) | ST-VULBAS-OUEST | 400 | 2300 | 2400 | 2400 | 2400 | [5 empty] | 0.562 | 5.705 | 70.374 | 18.713
LIT 400kV N0 1 CHAINGY - VERGER | 17T000000020072S | RTE | CHAINGY | VERGER | 400 | 1332 | 1796 | 1796 | 2098 | [5 empty] | 0.716 | 7.287 | 90.074 | 23.926
LIT 400kV N0 1 CHAMBRY - MERY-SUR-SEINE | 17T000000019828Y | RTE | CHAMBRY | MERY-SUR-SEINE | 400 | 1812 | 1988 | 1988 | 2124 | [5 empty] | 4.148 | 32.015 | 310.662 | 93.177
LIT 400kV N0 1 CHAMBRY - PENCHARD | 17T000000019829W | RTE | CHAMBRY | PENCHARD | 400 | 1988 | 2122 | 2122 | 2258 | [5 empty] | 0.201 | 1.622 | 15.872 | 4.722
LIT 400kV N0 1 CHAMPAGNIER - VAUJANY | 17T000000021411R | RTE | CHAMPAGNIER | VAUJANY | 400 | 2600 | 2700 | 2700 | 2800 | [5 empty] | 0.667 | 9.296 | 117.086 | 30.75
LIT 400kV N0 1 CHANCEAUX - DISTRE | 17T000000020133Y | RTE | CHANCEAUX | DISTRE | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 2.318 | 24.1 | 298.8 | 79.08
LIT 400kV N0 1 CHANCEAUX - LARCAY | 17T000000020134W | RTE | CHANCEAUX | LARCAY | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.445 | 5.843 | 96.662 | 22.164
LIT 400kV N0 1 CHANCEAUX - QUINTES (LES) | 17T000000020135U | RTE | CHANCEAUX | QUINTES (LES) | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.191 | 15.651 | 259.536 | 59.408
LIT 400kV N0 1 CHANCEAUX - VILLERBON | 17T000000020136S | RTE | CHANCEAUX | VILLERBON | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 1.912 | 19.401 | 240.362 | 89.28
LIT 400KV N0 1 CHARPENAY - ECHALAS | 17T000000020258E | RTE | CHARPENAY | ECHALAS | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.526 | 9.604 | 129.056 | 32.89
LIT 400kV N0 1 CHARPENAY - GREPILLES | 17T000000020259C | RTE | CHARPENAY | GREPILLES | 400 | 2168 | 2308 | 2308 | 2448 | [5 empty] | 1.777 | 17.251 | 215.686 | 57.026
LIT 400kV N0 1 CHARPENAY - ST-VULBAS-OUEST | 17T000000020261P | RTE | CHARPENAY | ST-VULBAS-OUEST | 400 | 2300 | 2450 | 2450 | 2600 | [5 empty] | 1.696 | 17.199 | 212.9 | 53.537
LIT 400kV N0 1 CHESNOY (LE) - CIROLLIERS | 17T000000020417K | RTE | CHESNOY (LE) | CIROLLIERS | 400 | 1022 | 1614 | 1614 | 1956 | [5 empty] | 1.823 | 20.419 | 197.822 | 58.648
LIT 400kV N0 1 CHESNOY (LE) - MERY-SUR-SEINE | 17T000000020418I | RTE | CHESNOY (LE) | MERY-SUR-SEINE | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 2.465 | 24.978 | 309.748 | 82.163
LIT 400kV N0 1 CHESNOY (LE) - MORBRAS | 17T000000020419G | RTE | CHESNOY (LE) | MORBRAS | 400 | 2300 | 2522 | 2522 | 2696 | [5 empty] | 1.451 | 15.877 | 162.826 | 47.256
LIT 400kV N0 1 CHESNOY (LE) - TABARDERIE | 17T000000020421T | RTE | CHESNOY (LE) | TABARDERIE | 400 | 2138 | 2356 | 2356 | 2522 | [5 empty] | 2.847 | 31.537 | 314.032 | 91.731
LIT 400kV N0 1 CHESNOY (LE) - VILLECHETIVE | 17T000000020442L | RTE | CHESNOY (LE) | VILLECHETIVE | 400 | 1410 | 1808 | 1808 | 2116 | [5 empty] | 2.198 | 24.353 | 242.22 | 71.239
LIT 400kV N0 1 CHEVALET - GAVRELLE | 17T-FR-00000012B | RTE | CHEVALET | GAVRELLE | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 0.595 | 7.809 | 129.324 | 67.14
LIT 400kV N0 1 CHEVALET - LATENA | 17T000000020496Z | RTE | CHEVALET | LATENA | 400 | 2570 | 2718 | 2718 | 2914 | [5 empty] | 1.977 | 20.03 | 249.706 | 65.954
LIT 400kV N0 1 CHEVALET - WARANDE | 17T-FR-000000139 | RTE | CHEVALET | WARANDE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 3.115 | 31.604 | 391.644 | 29.616
LIT 400kV N0 1 CIROLLIERS - GATINAIS | 17T000000020614I | RTE | CIROLLIERS | GATINAIS | 400 | 2300 | 2522 | 2522 | 2696 | [5 empty] | 1.068 | 14.027 | 232.516 | 19.64
LIT 400kV N0 1 CIROLLIERS - VILLEJUST | 17T000000020615G | RTE | CIROLLIERS | VILLEJUST | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.609 | 6.8 | 65.536 | 53.455
LIT 400kV N0 1 CLERAC - CUBNEZAIS | 17T0000000207283 | RTE | CLERAC | CUBNEZAIS | 400 | 1850 | 2194 | 2194 | 2370 | [5 empty] | 0.661 | 7.126 | 74.388 | 127.98
LIT 400kV N0 1 CLERAC - PLAUD | 17T0000000207291 | RTE | CLERAC | PLAUD | 400 | 2585 | 2633 | 2633 | 2715 | [5 empty] | 3.972 | 44.447 | 429.556 | 40.341
LIT 400kV N0 1 COCHE (LA) - PRAZ-ST-ANDRE | 17T-FR-00000045X | RTE | COCHE (LA) | PRAZ-ST-ANDRE | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 1.237 | 17.543 | 113.486 | 91
LIT 400kV N0 1 CORDEMAIS-P - LOUISFERT (poste F) | 17T000000021059F | RTE | CORDEMAIS-POSTE | LOUISFERT | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 1.671 | 16.933 | 210.436 | 150.881
LIT 400kV N0 1 CORDEMAIS-POSTE - GALOREAUX (LES) | 17T000000016584E | RTE | CORDEMAIS-POSTE | GALOREAUX (LES) | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 2.738 | 26.79 | 359.872 | 55.189
LIT 400kV N0 1 CORNIER - GENISSIAT-POSTE | 17T000000021173H | RTE | CORNIER | GENISSIAT-POSTE | 400 | 2304 | 2462 | 2462 | 2654 | [5 empty] | 0.764 | 11.675 | 172.588 | 68.868
LIT 400kV N0 1 CORNIER - MONTAGNY-LES-LANCHES | 17T-FR-00000066P | RTE | CORNIER | MONTAGNY-LES-LANCHES | 400 | 3465 | 3544 | 3544 | 3575 | [5 empty] | 1.649 | 21.038 | 267.65 | 90.713
LIT 400kV N0 1 COULANGE - PIVOZ-CORDIER | 17T000000021291B | RTE | COULANGE | PIVOZ-CORDIER | 400 | 2144 | 2284 | 2284 | 2448 | [5 empty] | 2.725 | 27.563 | 342.054 | 90.708
LIT 400kV N0 1 COULANGE - TAVEL | 17T0000000212929 | RTE | COULANGE | TAVEL | 400 | 2168 | 2308 | 2308 | 2448 | [5 empty] | 2.283 | 21.794 | 283.372 | 45.273
LIT 400kV N0 1 COULANGE - TRICASTIN-POSTE (LE) | 17T0000000212937 | RTE | COULANGE | TRICASTIN-POSTE (LE) | 400 | 3465 | 3544 | 3544 | 3575 | [5 empty] | 1.371 | 13.485 | 168.124 | 90.713
LIT 400kV N0 1 CRENEY - MERY-SUR-SEINE | 17T000000021523G | RTE | CRENEY | MERY-SUR-SEINE | 400 | 2366 | 2400 | 2400 | 2600 | [5 empty] | 1.172 | 9.065 | 88.438 | 83.925
LIT 400kV N0 1 CRENEY - REVIGNY | 17T-FR-00000056S | RTE | CRENEY | REVIGNY | 400 | 1684 | 1854 | 1854 | 1986 | [5 empty] | 2.595 | 27.828 | 292 | 40.8
LIT 400kV N0 1 CRENEY - VIELMOULIN | 17T000000021524E | RTE | CRENEY | VIELMOULIN | 400 | 2946 | 3144 | 3144 | 3344 | [5 empty] | 5.532 | 42.281 | 409.788 | 59.949
LIT 400kV N0 1 CREYS - GENISSIAT-POSTE | 17T000000021540G | RTE | CREYS | GENISSIAT-POSTE | 400 | 2946 | 3144 | 3144 | 3344 | [5 empty] | 1.112 | 16.141 | 216.056 | 21.051
LIT 400kV N0 1 CREYS - GRANDE-ILE | 17T0000000215391 | RTE | CREYS | GRANDE-ILE | 400 | 2750 | 2875 | 2875 | 3000 | [5 empty] | 1.271 | 18.454 | 229.688 | 52.885
LIT 400kV N0 1 CREYS - ST-VULBAS-OUEST | 17T000000021541E | RTE | CREYS | ST-VULBAS-OUEST | 400 | 2946 | 3144 | 3144 | 3344 | [5 empty] | 0.445 | 6.452 | 80.274 | 60.459
LIT 400kV N0 1 CUBNEZAIS - DONZAC | 17T000000021765T | RTE | CUBNEZAIS | DONZAC | 400 | 2374 | 2522 | 2522 | 2624 | [5 empty] | 3.748 | 49.276 | 817.884 | 63.067
LIT 400kV N0 1 CUBNEZAIS - SAUCATS | 17T000000021766R | RTE | CUBNEZAIS | SAUCATS | 400 | 3150 | 3307 | 3307 | 3465 | [5 empty] | 1.876 | 19.02 | 235.794 | 210.752
LIT 400kV N0 1 DAMBRON - GATINAIS | 17T000000022014W | RTE | DAMBRON | GATINAIS | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.848 | 11.133 | 184.472 | 55.1
LIT 400kV N0 1 DAMBRON - VERGER | 17T000000022015U | RTE | DAMBRON | VERGER | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 1.664 | 16.881 | 209.196 | 116.318
LIT 400kV N0 1 DAMBRON-YVELINES-OUEST | 17T000000022016S | RTE | DAMBRON | YVELINES-OUEST | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 3.477 | 35.298 | 438.904 | 42.736
LIT 400kV N0 1 DISTRE - GALOREAUX (LES) | 17T0000000222843 | RTE | DISTRE | GALOREAUX (LES) | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 1.783 | 18.026 | 225.798 | 46.472
LIT 400kV N0 1 DISTRE - JUMEAUX (LES) | 17T0000000222851 | RTE | DISTRE | JUMEAUX (LES) | 400 | 2494 | 2716 | 2716 | 2872 | [5 empty] | 1.395 | 14.155 | 174.912 | 98.933
LIT 400kV N0 1 DISTRE - PICOCHERIE (LA) | 17T000000022287Y | RTE | DISTRE | PICOCHERIE (LA) | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 2.91 | 30.086 | 373.12 | 46.472
LIT 400kV N0 1 DOMLOUP - LAUNAY | 17T0000000223386 | RTE | DOMLOUP | LAUNAY | 400 | 2494 | 2676 | 2676 | 2778 | [5 empty] | 1.411 | 18.548 | 307.582 | 48.566
LIT 400kV N0 1 DOMLOUP - LOUISFERT (poste F) | 17T0000000223394 | RTE | DOMLOUP | LOUISFERT | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.469 | 14.91 | 184.07 | 43.829
LIT 400kV N0 1 DOMLOUP - OUDON | 17T000000022340J | RTE | DOMLOUP | OUDON | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.921 | 11.633 | 191.51 | 111.701
LIT 400kV N0 1 DOMLOUP-PLAINE HAUTE | 17T000000022341H | RTE | DOMLOUP | PLAINE HAUTE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 3.396 | 36.665 | 394.792 | 70.591
LIT 400kV N0 1 DONZAC - LESQUIVE | 17T0000000223807 | RTE | DONZAC | LESQUIVE | 400 | 3255 | 3600 | 3600 | 3780 | [5 empty] | 1.007 | 13.151 | 215.64 | 89.931
LIT 400KV N0 1 ECHALAS - PIVOZ-CORDIER | 17T0000000226083 | RTE | ECHALAS | PIVOZ-CORDIER | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.268 | 4.89 | 65.712 | 16.747
LIT 400kV N0 1 EGUZON - MARMAGNE | 17T000000022693N | RTE | EGUZON | MARMAGNE | 400 | 2332 | 2582 | 2582 | 2716 | [5 empty] | 2.742 | 30.811 | 295.634 | 85.196
LIT 400kV N0 1 EGUZON - PLAUD | 17T000000022694L | RTE | EGUZON | PLAUD | 400 | 1186 | 1644 | 1644 | 1968 | [5 empty] | 2.64 | 29.543 | 283.666 | 227.31
LIT 400kV N0 1 EGUZON - RUEYRES | 17T000000022695J | RTE | EGUZON | RUEYRES | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 6.694 | 73.668 | 801.766 | 76
LIT 400kV N0 1 EGUZON - VALDIVIENNE | 17T000000022696H | RTE | EGUZON | VALDIVIENNE | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 1.518 | 19.985 | 331.834 | 144.534
LIT 400kV N0 1 EGUZON - VERGER | 17T000000022697F | RTE | EGUZON | VERGER | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 4.171 | 45.846 | 525.448 | 75.954
LIT 400kV N0 1 FAUX-FRESNAY-MERY-SUR-SEINE | 17T000001005111N | RTE | FAUX FRENAIS | MERY-SUR-SEINE | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 0.473 | 5.063 | 53.26 | 15.262
LIT 400KV N0 1 FAUX-FRESNAY-VESLE | 17T000001005112L | RTE | FAUX FRENAIS | VESLE | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 2.037 | 21.818 | 229,238‬ | 65.727
LIT 400kV N0 1 FRASNE - GENISSIAT-POSTE | 17T-FR-000000511 | RTE | FRASNE | GENISSIAT-POSTE | 400 | 2070 | 2282 | 2282 | 2400 | [5 empty] | 3.012 | 36.863 | 314.544 | 71.386
LIT 400kV N0 1 FRASNE - MAMBELIN | 17T-FR-00000053Y | RTE | FRASNE | MAMBELIN | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 2.068 | 22.621 | 260.32 | 52
LIT 400kV N0 1 FRUGES - MANDARINS | 17T000000023608Z | RTE | FRUGES | MANDARINS | 400 | 3195 | 3561 | 3561 | 3780 | [5 empty] | 1.037 | 13.637 | 226.322 | 88.758
LIT 400kV N0 1 GATINAIS - GAUGLIN | 17T000000023965B | RTE | GATINAIS | GAUGLIN | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.74 | 22.883 | 379.664 | 44.838
LIT 400kV N0 1 GATINAIS - TABARDERIE | 17T0000000239669 | RTE | GATINAIS | TABARDERIE | 400 | 3195 | 3561 | 3561 | 3780 | [5 empty] | 0.899 | 11.804 | 195.626 | 88.736
LIT 400kV N0 1 GAUDIERE (LA) - ISSEL | 17T0000000239774 | RTE | GAUDIERE (LA) | ISSEL | 400 | 2176 | 2400 | 2400 | 2576 | [5 empty] | 1.775 | 17.931 | 224.964 | 175.186
LIT 400kV N0 1 GENISSIAT-POSTE - VIELMOULIN | 17T000000024077Z | RTE | GENISSIAT-POSTE | VIELMOULIN | 400 | 2200 | 2556 | 2556 | 2864 | [5 empty] | 3.545 | 51.485 | 641.618 | 168.798
LIT 400kV N0 1 GRANZAY - JUMEAUX (LES) | 17T000000024379J | RTE | GRANZAY | JUMEAUX (LES) | 400 | 3072 | 3414 | 3414 | 3598 | [5 empty] | 2.364 | 24.314 | 301.63 | 64.884
LIT 400kV N0 1 GRANZAY - PREGUILLAC | 17T000000024380Y | RTE | GRANZAY | PREGUILLAC | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.35 | 19.588 | 243.978 | 54.452
LIT 400kV N0 1 GRANZAY - ROM | 17T000000024381W | RTE | GRANZAY | ROM | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 1.1 | 14.465 | 240.174 | 79.955
LIT 400kV N0 1 GROSNE - ST-VULBAS-OUEST | 17T000000024493L | RTE | GROSNE | ST-VULBAS-OUEST | 400 | 2138 | 2356 | 2356 | 2522 | [5 empty] | 3.567 | 39.288 | 397.61 | 2.84
LIT 400kV N0 1 GROSNE - VIELMOULIN | 17T000000024494J | RTE | GROSNE | VIELMOULIN | 400 | 2300 | 2450 | 2450 | 2600 | [5 empty] | 2.549 | 28.582 | 273.756 | 131.583
LIT 400kV N0 1 HENRI-PAUL - ST-VULBAS-OUEST | 17T000000024660S | RTE | HENRI-PAUL | ST-VULBAS-OUEST | 400 | 3294 | 3622 | 3622 | 3780 | [5 empty] | 2.637 | 37.126 | 536.286 | 66.068
LIT 400kV N0 1 HENRI-PAUL - VIELMOULIN | 17T000000024661Q | RTE | HENRI-PAUL | VIELMOULIN | 400 | 2104 | 2300 | 2300 | 2400 | [5 empty] | 1.349 | 17.72 | 293.61 | 54.154
LIT 400kV N0 1 HERSE(LA) - LATENA | 17T000000024862G | RTE | HERSE(LA) | LATENA | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 1.229 | 12.468 | 154.358 | 61.754
LIT 400kV N0 1 HERSE(LA) - VILLEVAUDE | 17T000000024863E | RTE | HERSE(LA) | VILLEVAUDE | 400 | 2055 | 2277 | 2277 | 2458 | [5 empty] | 1.856 | 18.819 | 232.876 | 61.833
LIT 400kV N0 1 HOUDREVILLE - LOGELBACH | 17T-FR-000000163 | RTE | HOUDREVILLE | LOGELBACH | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 3.108 | 35.853 | 386.368 | 109.17
LIT 400kV N0 1 HOUDREVILLE - MERY-SUR-SEINE | 17T-FR-000000171 | RTE | HOUDREVILLE | MERY-SUR-SEINE | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 4.883 | 49.515 | 613.6 | 162.749
LIT 400kV N0 1 HOUDREVILLE - NEUVES-MAISONS | 17T000000024897Y | RTE | HOUDREVILLE | NEUVES-MAISONS | 400 | 2214 | 2450 | 2450 | 2630 | [5 empty] | 0.333 | 3.559 | 38.096 | 10.822
LIT 400kV N0 1 HOUDREVILLE - VINCEY | 17T-FR-00000019Y | RTE | HOUDREVILLE | VINCEY | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 0.818 | 8.953 | 101.822 | 28.055
LIT 400kV N0 1 ISSEL - VERFEIL | 17T000000025009A | RTE | ISSEL | VERFEIL | 400 | 2170 | 2400 | 2400 | 2574 | [5 empty] | 1.167 | 11.809 | 147.752 | 38.884
LIT 400kV N0 1 JONQUIERES - TAVEL | 17T000000025124A | RTE | JONQUIERES | TAVEL | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.656 | 7.267 | 101.018 | 25.04
LIT 400kV N0 1 LA GAUDIERE - RUEYRES | 17T0000000239782 | RTE | GAUDIERE (LA) | RUEYRES | 400 | 3150 | 3392 | 3392 | 3590 | [5 empty] | 5.16 | 58.181 | 607.944 | 96.657
LIT 400kV N0 1 LA GAUDIERE - TAMAREAU | 17T000000023980F | RTE | GAUDIERE (LA) | TAMAREAU | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 2.036 | 29.623 | 368.43 | 59.184
LIT 400kV N0 1 LATENA - VILLEVAUDE | 17T0000000255893 | RTE | LATENA | VILLEVAUDE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 3.063 | 31.059 | 384.498 | 82
LIT 400kV N0 1 LAUNAY - TAUTE | 17T000000025593C | RTE | LAUNAY | TAUTE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.641 | 21.58 | 358.31 | 82
LIT 400kV N0 1 LESQUIVE - VERFEIL | 17T000000025751K | RTE | LESQUIVE | VERFEIL | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.805 | 10.592 | 175.388 | 47.228
LIT 400kV N0 1 LIMEUX - PENLY (POSTE EVACUATION) | 17T000000025800X | RTE | LIMEUX | PENLY (POSTE EVACUATION) | 400 | 2196 | 2400 | 2400 | 2596 | [5 empty] | 0.708 | 12.09 | 210.688 | 30.365
LIT 400kV N0 1 LOGELBACH - MUHLBACH | 17T-FR-00000021A | RTE | LOGELBACH | MUHLBACH | 400 | 2196 | 2400 | 2400 | 2596 | [5 empty] | 0.91 | 9.249 | 113.708 | 10.823
LIT 400kV N0 1 LONNY - MAZURES | 17T0000000259465 | RTE | LONNY | MAZURES | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.325 | 3.36 | 40.118 | 10.77
LIT 400kV N0 1 LONNY - SEUIL | 17T-FR-00000068L | RTE | LONNY | SEUIL | 400 | 3639 | 3894 | 3894 | 4149 | [5 empty] | 0.711 | 11.811 | 204.594 | 75.667
LIT 400kV N0 1 LONNY - VESLE | 17T-FR-000000260 | RTE | LONNY | VESLE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.193 | 20.013 | 347.576 | 118.313
LIT 400kV N0 1 LONNY-MOULAINE | 17T-FR-000000228 | RTE | LONNY | MOULAINE | 400 | 3639 | 3894 | 3894 | 4149 | [5 empty] | 2.26 | 29.7 | 491.268 | 43.688
LIT 400kV N0 1 MAMBELIN - SIERENTZ | 17T-FR-00000054W | RTE | MAMBELIN | SIERENTZ | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 2.35 | 24.592 | 264.894 | 28.604
LIT 400kV N0 1 MANDARINS - WARANDE | 17T0000000263213 | RTE | MANDARINS | WARANDE | 400 | 3294 | 3622 | 3622 | 3780 | [5 empty] | 0.572 | 7.547 | 124.334 | 33.049
LIT 400kV N0 1 MARLENHEIM - SCHEER | 17T000000026426Q | RTE | MARLENHEIM | SCHEER | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.663 | 8.703 | 144.158 | 33.048
LIT 400kV N0 1 MARLENHEIM-VIGY | 17T000000026427O | RTE | MARLENHEIM | VIGY | 400 | 1838 | 2036 | 2036 | 2140 | [5 empty] | 2.678 | 36.336 | 593.074 | 86.085
LIT 400kV N0 1 MARMAGNE - TABARDERIE | 17T000000026441U | RTE | MARMAGNE | TABARDERIE | 400 | 1410 | 1890 | 1890 | 2114 | [5 empty] | 3.753 | 29.361 | 291.146 | 90.623
LIT 400kV N0 1 MARQUIS (LE) - SAUCATS | 17T000000027102A | RTE | MARQUIS (LE) | SAUCATS | 400 | 1677 | 1875 | 1875 | 2100 | [5 empty] | 1.595 | 17.587 | 179.91 | 6.805
LIT 400kV N0 1 MENUEL - TAUTE | 17T000000026641M | RTE | MENUEL | TAUTE | 400 | 2662 | 2878 | 2878 | 2996 | [5 empty] | 0.72 | 9.468 | 157.206 | 14.3
LIT 400kV N0 1 MENUEL - TOLLEVAST | 17T000000026662E | RTE | MENUEL | TOLLEVAST | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.428 | 4.356 | 53.462 | 36
LIT 400kV N0 1 MERY-SUR-SEINE - VESLE | 17T-FR-00000028X | RTE | MERY-SUR-SEINE | VESLE | 400 | 2600 | 2700 | 2700 | 2800 | [5 empty] | 2.504 | 26.819 | 281.696 | 42.23
LIT 400kV N0 1 MERY-SUR-SEINE - VIELMOULIN | 17T000000026169K | RTE | MERY-SUR-SEINE | VIELMOULIN | 400 | 2600 | 2700 | 2700 | 2800 | [5 empty] | 3.149 | 45.724 | 569.77 | 42.21
LIT 400kV N0 1 MEZEROLLES - TILLEUL | 17T000000026732J | RTE | MEZEROLLES | TILLEUL | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 2.123 | 21.523 | 266.674 | 17.274
LIT 400kV N0 1 MEZEROLLES-YVELINES-OUEST | 17T000000026733H | RTE | MEZEROLLES | YVELINES-OUEST | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.518 | 5.251 | 65.122 | 70.228
LIT 400kV N0 1 MOLIERE - OUDON | 17T000000026907A | RTE | MOLIERE | OUDON | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.15 | 14.508 | 239.032 | 46.857
LIT 400kV N0 1 MOLIERE - QUINTES (LES) | 17T0000000269088 | RTE | MOLIERE | QUINTES (LES) | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.984 | 12.421 | 204.536 | 14.948
LIT 400kV N0 1 MONTEZIC (POSTE EXTERIEUR) - RUEYRES | 17T000000027159I | RTE | MONTEZIC (POSTE EXTERIEUR) | RUEYRES | 400 | 1677 | 1875 | 1875 | 2100 | [5 empty] | 0.163 | 2.758 | 19.49 | 0
LIT 400kV N0 1 MORBRAS - VILLEVAUDE | 17T0000000269452 | RTE | MORBRAS | VILLEVAUDE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.244 | 3.966 | 74.712 | 15.228
LIT 400kV N0 1 MOULAINE - VIGY | 17T-FR-00000029V | RTE | MOULAINE | VIGY | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.234 | 16.217 | 268.942 | 61.622
LIT 400kV N0 1 MUHLBACH - SCHEER | 17T000000027264L | RTE | MUHLBACH | SCHEER | 400 | 2202 | 2426 | 2426 | 2598 | [5 empty] | 1.59 | 17.975 | 215.35 | 0
LIT 400kV N0 1 MUHLBACH - VINCEY | 17T-FR-000000325 | RTE | MUHLBACH | VINCEY | 400 | 2055 | 2277 | 2277 | 2458 | [5 empty] | 3.195 | 36.108 | 397.53 | 111.227
LIT 400kV N0 1 MUHLBACH-SIERENTZ | 17T-FR-000000317 | RTE | MUHLBACH | SIERENTZ | 400 | 2202 | 2426 | 2426 | 2598 | [5 empty] | 0.959 | 10.713 | 115.74 | 32.691
LIT 400kV N0 1 NEOULES - REALTOR | 17T0000000273948 | RTE | NEOULES | REALTOR | 400 | 2006 | 2192 | 2192 | 2336 | [5 empty] | 2.16 | 20.427 | 256.624 | 68.288
LIT 400kV N0 1 NEOULES - TRANS | 17T0000000273956 | RTE | NEOULES | TRANS | 400 | 2128 | 2326 | 2326 | 2482 | [5 empty] | 1.357 | 13.765 | 170.198 | 45.205
LIT 400kV N0 1 OUDON - QUINTES (LES) | 17T000000027599R | RTE | OUDON | QUINTES (LES) | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 2.128 | 26.892 | 443.954 | 100.927
LIT 400kV N0 1 OUDON - TAUTE | 17T000000027600V | RTE | OUDON | TAUTE | 400 | 3900 | 4050 | 4050 | 4200 | [5 empty] | 3.26 | 42.869 | 711.792 | 163
LIT 400kV N0 1 PICOCHERIE (LA) - VILLERBON | 17T000000028135R | RTE | PICOCHERIE (LA) | VILLERBON | 400 | 2232 | 2448 | 2448 | 2666 | [5 empty] | 0.887 | 9.007 | 111.106 | 29.576
LIT 400kV N0 1 PLAN-D ORGON - TAVEL | 17T000000027796P | RTE | PLAN-D ORGON | TAVEL | 400 | 3192 | 3489 | 3489 | 3723 | [5 empty] | 0.832 | 10.94 | 181.59 | 41.812
LIT 400kV N0 1 PLESSIS-GASSOT - PENCHARD | 17T000000027707D | RTE | PLESSIS-GASSOT | PENCHARD | 400 | 1988 | 2122 | 2122 | 2258 | [5 empty] | 1.387 | 11.335 | 112.03 | 33.225
LIT 400kV N0 1 PLESSIS-GASSOT - SAUSSET | 17T000000027708B | RTE | PLESSIS-GASSOT | SAUSSET | 400 | 2300 | 2522 | 2522 | 2696 | [5 empty] | 0.425 | 4.707 | 47.072 | 13.828
LIT 400kV N0 1 PLESSIS-GASSOT - TERRIER | 17T0000000277099 | RTE | PLESSIS-GASSOT | TERRIER | 400 | 2300 | 2522 | 2522 | 2696 | [5 empty] | 0.805 | 9.079 | 108.718 | 29.084
LIT 400kV N0 1 PRAZ-ST-ANDRE - PIQUAGE A LA PRAZ-ST-ANDRE | 17T000000935461Y | RTE | PRAZ-ST-ANDRE | PIQUAGE A LA PRAZ-ST-ANDRE | 400 | 1500 | 1705 | 1705 | 1800 | [5 empty] | 0.003 | 0.058 | 0.712 | 0.17
LIT 400kV N0 1 PRAZ-ST-ANDRE - SUPER-BISSORTE | 17T0000000276297 | RTE | PRAZ-ST-ANDRE | SUPER-BISSORTE | 400 | 1300 | 1300 | 1300 | 1300 | [5 empty] | 0.036 | 0.22 | 28.338 | 0.998
LIT 400kV N0 1 PRIONNET - T.SUP / PRION - TAVEL | 17T000000028362G | RTE | PRIONNET | T.SUP / PRION - TAVEL | 400 | 3592 | 3886 | 3886 | 4094 | [5 empty] | 0.01 | 0.187 | 2.476 | 0.635
LIT 400kV N0 1 REALTOR - TAVEL | 17T0000000285377 | RTE | REALTOR | TAVEL | 400 | 2128 | 2326 | 2326 | 2482 | [5 empty] | 2.735 | 27.716 | 343.702 | 91.947
LIT 400kV N0 1 REMISE - TERRIER | 17T0000000285814 | RTE | REMISE | TERRIER | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.576 | 7.565 | 124.904 | 28.714
LIT 400kV N0 1 REVIGNY - VIGY | 17T-FR-000000341 | RTE | REVIGNY | VIGY | 400 | 2196 | 2422 | 2422 | 2596 | [5 empty] | 3.893 | 41.123 | 457.094 | 127.788
LIT 400kV N0 1 ROM - VALDIVIENNE | 17T000000028730D | RTE | ROM | VALDIVIENNE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.969 | 12.737 | 211.484 | 48.872
LIT 400kV N0 1 ROUGEMONTIER - TILLEUL | 17T000000028766T | RTE | ROUGEMONTIER | TILLEUL | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 1.192 | 12.086 | 149.636 | 41.165
LIT 400kV N0 1 ROUGEMONTIER - TOURBE | 17T000000028767R | RTE | ROUGEMONTIER | TOURBE | 400 | 3416 | 3622 | 3622 | 3780 | [5 empty] | 1.749 | 25.373 | 316.444 | 83.23
LIT 400kV N0 1 SAUSSET - VILLEVAUDE | 17T000000028936U | RTE | SAUSSET | VILLEVAUDE | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.354 | 3.946 | 38.684 | 11.483
LIT 400kV N0 1 SEREIN - VIELMOULIN | 17T0000000290032 | RTE | SEREIN | VIELMOULIN | 400 | 2138 | 2356 | 2356 | 2522 | [5 empty] | 2.952 | 33.112 | 317.63 | 95.23
LIT 400kV N0 1 SEREIN - VILLECHETIVE | 17T000000029005Z | RTE | SEREIN | VILLECHETIVE | 400 | 2138 | 2356 | 2356 | 2522 | [5 empty] | 1.119 | 12.273 | 125.084 | 36.396
LIT 400kV N0 1 SEUIL - VESLE | 17T-FR-00000069J | RTE | SEUIL | VESLE | 400 | 4200 | 4200 | 4200 | 4200 | [5 empty] | 0.491 | 8.348 | 145.658 | 33
LIT 400kV N0 1 ST-AVOLD - VIGY | 17T000000029130W | RTE | ST-AVOLD | VIGY | 400 | 1245 | 1245 | 1450 | 1450 | [5 empty] | 0.677 | 8.928 | 164.452 | 0.28
LIT 400kV N0 1 TAMAREAU - TAVEL | 17T0000000293396 | RTE | TAMAREAU | TAVEL | 400 | 4400 | 4500 | 4500 | 4500 | [5 empty] | 1.995 | 28.294 | 336.126 | 91
LIT 400kV N0 1 TAUTE - TERRETTE | 17T000000029341J | RTE | TAUTE | TERRETTE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.28 | 3.682 | 61.136 | 13.998
LIT 400kV N0 1 TAVEL - TRICASTIN-POSTE (LE) | 17T0000000293671 | RTE | TAVEL | TRICASTIN-POSTE (LE) | 400 | 2212 | 2380 | 2380 | 2498 | [5 empty] | 1.294 | 12.506 | 155.668 | 41.959
LIT 400kV N0 1 TERRETTE - TOURBE | 17T000000029377Z | RTE | TERRETTE | TOURBE | 400 | 3416 | 3622 | 3622 | 3780 | [5 empty] | 1.466 | 21.29 | 265.348 | 69.804
LIT 400kV N0 1 VERGER - VILLERBON | 17T000000029532C | RTE | VERGER | VILLERBON | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.805 | 8.172 | 100.984 | 26.844
LIT 400kV N0 1 VILLARODIN - PIQUAGE A LA PRAZ-ST-ANDRE | 17T-FR-00000046V | RTE | VILLARODIN | PIQUAGE A LA PRAZ-ST-ANDRE | 400 | 2585 | 2633 | 2633 | 2715 | [5 empty] | 0.356 | 5.038 | 32.49 | 11.475
LIT 400kV N0 1 WARANDE-WEPPES | 17T-FR-00000036Y | RTE | WARANDE | WEPPES | 400 | 3078 | 3266 | 3266 | 3458 | [5 empty] | 1.628 | 20.841 | 235.3 | 65.573
LIT 400kV N0 2 ALBERTVILLE - GRANDE-ILE | 17T-FR-00000058O | RTE | ALBERTVILLE | GRANDE-ILE | 400 | 3099 | 3441 | 3441 | 3741 | [5 empty] | 0.74 | 11.298 | 169.282 | 40.775
LIT 400kV N0 2 ARGOEUVES - CHEVALET | 17T000000015961F | RTE | ARGOEUVES | CHEVALET | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.833 | 10.936 | 181.15 | 42.23
LIT 400kV N0 2 ARGOEUVES - TERRIER | 17T0000000159827 | RTE | ARGOEUVES | TERRIER | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.686 | 22.134 | 366.4 | 84.037
LIT 400kV N0 2 ATTAQUES (LES) - MANDARINS | 17T0000000163049 | RTE | ATTAQUES (LES) | MANDARINS | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.21 | 2.76 | 45.736 | 10.484
LIT 400kV N0 2 ATTAQUES (LES) - WARANDE | 17T0000000163057 | RTE | ATTAQUES (LES) | WARANDE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.365 | 4.799 | 79.504 | 18.296
LIT 400kV N0 2 AVELIN - WARANDE | 17T-FR-00000003C | RTE | AVELIN | WARANDE | 400 | 3078 | 3266 | 3266 | 3458 | [5 empty] | 2.172 | 27.866 | 316.88 | 86.764
LIT 400kV N0 2 AVELIN-MASTAING | 17T-FR-000000058 | RTE | AVELIN | MASTAING | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.681 | 8.954 | 148.672 | 34.067
LIT 400kV N0 2 AVOINE (POSTE 400 kV) - DISTRE | 17T000000016635N | RTE | AVOINE (POSTE 400 KV) | DISTRE | 400 | 3196 | 3488 | 3488 | 3582 | [5 empty] | 0.511 | 6.624 | 81.742 | 21.629
LIT 400kV N0 2 AVOINE (POSTE 400 kV) - GRILLE-AVOINE | 17T000000016636L | RTE | AVOINE (POSTE 400 KV) | GRILLE-AVOINE | 400 | 1604 | 1604 | 1700 | 1700 | [5 empty] | 0.01 | 0.159 | 6.726 | 0.447
LIT 400kV N0 2 AVOINE (POSTE 400 kV) - LARCAY | 17T000000016637J | RTE | AVOINE (POSTE 400 KV) | LARCAY | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.008 | 13.253 | 219.792 | 50.36
LIT 400kV N0 2 BAIXAS - LA GAUDIERE | 17T-FR-00000039S | RTE | BAIXAS | GAUDIERE (LA) | 400 | 4400 | 4500 | 4500 | 4500 | [5 empty] | 1.565 | 22.203 | 263.746 | 71.263
LIT 400kV N0 2 BARNABOS - ROUGEMONTIER | 17T000000017238S | RTE | BARNABOS | ROUGEMONTIER | 400 | 3416 | 3622 | 3622 | 3780 | [5 empty] | 1.057 | 15.342 | 191.068 | 50.274
LIT 400kV N0 2 BARNABOS - TERRIER | 17T000000017239Q | RTE | BARNABOS | TERRIER | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 2.137 | 28.109 | 466.858 | 106.841
LIT 400kV N0 2 BARNABOS - VAUPALIERE (LA) | 17T0000000172404 | RTE | BARNABOS | VAUPALIERE (LA) | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.438 | 5.752 | 95.118 | 21.813
LIT 400kV N0 2 BARNABOS-PENLY (POSTE EVACUATION) | 17T000000017236W | RTE | BARNABOS | PENLY (POSTE EVACUATION) | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.707 | 12.044 | 210.228 | 47.082
LIT 400kV N0 2 BARNABOS-REMISE | 17T000000017237U | RTE | BARNABOS | REMISE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.711 | 22.484 | 372.898 | 86.145
LIT 400kV N0 2 BAYET - GREPILLES | 17T0000000174008 | RTE | BAYET | GREPILLES | 400 | 2130 | 2374 | 2374 | 2576 | [5 empty] | 2.123 | 21.52 | 266.788 | 70.752
LIT 400kV N0 2 BAYET - MARMAGNE | 17T0000000174016 | RTE | BAYET | MARMAGNE | 400 | 2130 | 2300 | 2300 | 2400 | [5 empty] | 3.71 | 37.594 | 466.21 | 123.205
LIT 400kV N0 2 BAYET - RULHAT | 17T000000017422Z | RTE | BAYET | RULHAT | 400 | 2600 | 2700 | 2700 | 2800 | [5 empty] | 1.039 | 13.665 | 226.724 | 52.395
LIT 400kV N0 2 BAYET-ST-ELOI | 17T000000017423X | RTE | BAYET | ST-ELOI | 400 | 2800 | 3000 | 3000 | 3100 | [5 empty] | 1.712 | 22.502 | 373.17 | 85.603
LIT 400kV N0 2 BEAUMONT-MONTEUX - CHAFFARD (LE) | 17T0000000169458 | RTE | BEAUMONT-MONTEUX | CHAFFARD (LE) | 400 | 3465 | 3544 | 3544 | 3575 | [5 empty] | 2.261 | 22.922 | 283.972 | 75.994
LIT 400kV N0 2 BEAUMONT-MONTEUX - COULANGE | 17T0000000169466 | RTE | BEAUMONT-MONTEUX | COULANGE | 400 | 3465 | 3544 | 3544 | 3575 | [5 empty] | 1.715 | 19.416 | 223.21 | 61.247
LIT 400kV N0 2 BEZAUMONT - HOUDREVILLE | 17T-FR-000000082 | RTE | BEZAUMONT | HOUDREVILLE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.031 | 13.545 | 224.574 | 51.462
LIT 400kV N0 2 BEZAUMONT - VIGY | 17T-FR-000000090 | RTE | BEZAUMONT | VIGY | 400 | 3294 | 3622 | 3622 | 3780 | [5 empty] | 0.887 | 11.644 | 192.584 | 44.179
LIT 400kV N0 2 BIANCON - TRANS | 17T000000017835A | RTE | BIANCON | TRANS | 400 | 2128 | 2326 | 2326 | 2482 | [5 empty] | 0.936 | 9.487 | 117.652 | 31.212
LIT 400kV N0 2 BOCTOIS - MERY-SUR-SEINE | 17T0000000180407 | RTE | BOCTOIS | MERY-SUR-SEINE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.714 | 9.373 | 155.084 | 35.572
LIT 400kV N0 2 BOCTOIS - MORBRAS | 17T0000000180415 | RTE | BOCTOIS | MORBRAS | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.606 | 21.112 | 350.254 | 77.983
LIT 400kV N0 2 BRAUD - CUBNEZAIS | 17T000000018503U | RTE | BRAUD | CUBNEZAIS | 400 | 3072 | 3414 | 3414 | 3598 | [5 empty] | 0.642 | 9.318 | 115.878 | 30.529
LIT 400kV N0 2 BRAUD - PREGUILLAC | 17T000000018504S | RTE | BRAUD | PREGUILLAC | 400 | 3072 | 3414 | 3414 | 3598 | [5 empty] | 0.994 | 14.43 | 179.714 | 47.366
LIT 400kV N0 2 BROC-CARROS (LE)-BIANCON | 17T0000000167595 | RTE | BROC-CARROS (LE) | BIANCON | 400 | 2006 | 2192 | 2192 | 2336 | [5 empty] | 1.665 | 15.592 | 195.998 | 51.487
LIT 400kV N0 2 CANTEGRIT - SAUCATS | 17T-FR-000000406 | RTE | CANTEGRIT | SAUCATS | 400 | 2690 | 2822 | 2822 | 2936 | [5 empty] | 1.943 | 25.186 | 239.634 | 72.59
LIT 400kV N0 2 CAZARIL - MARSILLON | 17T000000019791V | RTE | CAZARIL | MARSILLON | 400 | 3316 | 3622 | 3622 | 3780 | [5 empty] | 2.09 | 29.12 | 465.45 | 101.657
LIT 400kV N0 2 CAZARIL - VERFEIL | 17T000000019792T | RTE | CAZARIL | VERFEIL | 400 | 3255 | 3600 | 3600 | 3780 | [5 empty] | 2.412 | 32.015 | 528.254 | 121.341
LIT 400kV N0 2 CERGY-MEZEROLLES | 17T000000019868M | RTE | CERGY | MEZEROLLES | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.99 | 10.227 | 120.576 | 32.714
LIT 400kV N0 2 CERGY-TERRIER | 17T000000019869K | RTE | CERGY | TERRIER | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 0.879 | 9.253 | 102.972 | 28.712
LIT 400kV N0 2 CHAFFARD (LE) - CHAMPAGNIER | 17T0000000200234 | RTE | CHAFFARD (LE) | CHAMPAGNIER | 400 | 2110 | 2246 | 2246 | 2382 | [5 empty] | 2.248 | 27.612 | 296.112 | 84.001
LIT 400kV N0 2 CHAFFARD (LE)-GRANDE-ILE | 17T0000000200242 | RTE | CHAFFARD (LE) | GRANDE-ILE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.441 | 20.472 | 321.626 | 76.242
LIT 400kV N0 2 CHAFFARD (LE)-MIONS | 17T000000020026Z | RTE | CHAFFARD (LE) | MIONS | 400 | 2300 | 2450 | 2450 | 2600 | [5 empty] | 0.288 | 3.687 | 58.678 | 13.304
LIT 400kV N0 2 CHAFFARD (LE)-PIVOZ-CORDIER | 17T000000020027X | RTE | CHAFFARD (LE) | PIVOZ-CORDIER | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.293 | 14.857 | 170.62 | 47.327
LIT 400kV N0 2 CHAFFARD (LE)-ST-VULBAS-OUEST | 17T000000020028V | RTE | CHAFFARD (LE) | ST-VULBAS-OUEST | 400 | 2300 | 2400 | 2400 | 2400 | [5 empty] | 0.562 | 5.71 | 70.39 | 18.722
LIT 400kV N0 2 CHAINGY-VERGER | 17T000000020073Q | RTE | CHAINGY | VERGER | 400 | 1332 | 1796 | 1796 | 2098 | [5 empty] | 0.715 | 7.275 | 89.952 | 24.011
LIT 400kV N0 2 CHAMPAGNIER-VAUJANY | 17T000000021412P | RTE | CHAMPAGNIER | VAUJANY | 400 | 1812 | 1988 | 1988 | 2124 | [5 empty] | 0.667 | 9.29 | 117.016 | 26.413
LIT 400kV N0 2 CHANCEAUX - LARCAY | 17T000000020137Q | RTE | CHANCEAUX | LARCAY | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.445 | 5.839 | 96.612 | 22.164
LIT 400kV N0 2 CHANCEAUX-QUINTES (LES) | 17T000000020138O | RTE | CHANCEAUX | QUINTES (LES) | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.191 | 15.652 | 259.546 | 59.426
LIT 400kV N0 2 CHARPENAY-ECHALAS | 17T000000020282H | RTE | CHARPENAY | ECHALAS | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.533 | 9.712 | 131.074 | 32.882
LIT 400kV N0 2 CHARPENAY-GREPILLES | 17T000000020283F | RTE | CHARPENAY | GREPILLES | 400 | 2168 | 2308 | 2308 | 2448 | [5 empty] | 1.712 | 17.367 | 214.72 | 57.036
LIT 400kV N0 2 CHARPENAY-ST-VULBAS-OUEST | 17T000000020284D | RTE | CHARPENAY | ST-VULBAS-OUEST | 400 | 2300 | 2450 | 2450 | 2600 | [5 empty] | 1.711 | 17.374 | 214.7 | 56.986
LIT 400kV N0 2 CHESNOY (LE)-CIROLLIERS | 17T000000020443J | RTE | CHESNOY (LE) | CIROLLIERS | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 1.819 | 20.373 | 197.596 | 82.187
LIT 400kV N0 2 CHESNOY (LE)-MERY-SUR-SEINE | 17T000000020444H | RTE | CHESNOY (LE) | MERY-SUR-SEINE | 400 | 2300 | 2400 | 2400 | 2600 | [5 empty] | 2.468 | 25.046 | 309.706 | 47.267
LIT 400kV N0 2 CHESNOY (LE)-MORBRAS | 17T000000020445F | RTE | CHESNOY (LE) | MORBRAS | 400 | 2814 | 3110 | 3110 | 3338 | [5 empty] | 1.451 | 15.878 | 162.878 | 114.626
LIT 400kV N0 2 CHESNOY (LE)-TABARDERIE | 17T000000020446D | RTE | CHESNOY (LE) | TABARDERIE | 400 | 2814 | 3110 | 3110 | 3338 | [5 empty] | 1.854 | 26.679 | 339.146 | 115.433
LIT 400kV N0 2 CHEVALET - GAVRELLE | 17T-FR-000000147 | RTE | CHEVALET | GAVRELLE | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 0.598 | 7.859 | 130.17 | 83.793
LIT 400kV N0 2 CHEVALET - LATENA | 17T000000020497X | RTE | CHEVALET | LATENA | 400 | 2570 | 2718 | 2718 | 2914 | [5 empty] | 1.97 | 19.967 | 248.476 | 32.379
LIT 400kV N0 2 CHEVALET-WARANDE | 17T-FR-000000155 | RTE | CHEVALET | WARANDE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 3.113 | 31.59 | 391.498 | 53.85
LIT 400kV N0 2 CIROLLIERS - GATINAIS | 17T000000020616E | RTE | CIROLLIERS | GATINAIS | 400 | 2300 | 2522 | 2522 | 2696 | [5 empty] | 1.067 | 14.021 | 232.434 | 19.807
LIT 400kV N0 2 CIROLLIERS - VILLEJUST | 17T000000020617C | RTE | CIROLLIERS | VILLEJUST | 400 | 1812 | 1988 | 1988 | 2124 | [5 empty] | 0.614 | 6.865 | 66.07 | 21.904
LIT 400kV N0 2 CORDEMAIS-POSTE - DISTRE | 17T000000021060U | RTE | CORDEMAIS-POSTE | DISTRE | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 4.521 | 45.811 | 568.374 | 55.162
LIT 400kV N0 2 CORDEMAIS-POSTE - LOUISFERT (poste F) | 17T000000021061S | RTE | CORDEMAIS-POSTE | LOUISFERT | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 1.666 | 16.878 | 209.75 | 238.814
LIT 400kV N0 2 CORDEMAIS-POSTE - MARTYRE (LA) | 17T000000021082K | RTE | CORDEMAIS-POSTE | MARTYRE (LA) | 400 | 3456 | 3622 | 3622 | 3780 | [5 empty] | 7.083 | 72.149 | 900.732 | 41.841
LIT 400kV N0 2 COULANGE-PIVOZ-CORDIER | 17T0000000212953 | RTE | COULANGE | PIVOZ-CORDIER | 400 | 2168 | 2308 | 2308 | 2448 | [5 empty] | 2.706 | 27.369 | 339.694 | 45.546
LIT 400kV N0 2 COULANGE-TRICASTIN-POSTE (LE) | 17T0000000212961 | RTE | COULANGE | TRICASTIN-POSTE (LE) | 400 | 2168 | 2308 | 2308 | 2448 | [5 empty] | 1.404 | 13.77 | 171.78 | 45.546
LIT 400kV N0 2 CREYS-GENISSIAT-POSTE | 17T0000000215634 | RTE | CREYS | GENISSIAT-POSTE | 400 | 2946 | 3144 | 3144 | 3344 | [5 empty] | 1.113 | 16.161 | 201.458 | 21.051
LIT 400kV N0 2 CREYS-GRANDE-ILE | 17T0000000215626 | RTE | CREYS | GRANDE-ILE | 400 | 2600 | 2700 | 2700 | 2800 | [5 empty] | 1.271 | 18.452 | 229.666 | 52.924
LIT 400kV N0 2 CREYS-ST-VULBAS-OUEST | 17T0000000215642 | RTE | CREYS | ST-VULBAS-OUEST | 400 | 3150 | 3307 | 3307 | 3465 | [5 empty] | 0.445 | 6.448 | 80.224 | 187.57
LIT 400kV N0 2 CUBNEZAIS-DONZAC | 17T000000021767P | RTE | CUBNEZAIS | DONZAC | 400 | 2258 | 2400 | 2400 | 2600 | [5 empty] | 3.716 | 48.855 | 810.884 | 12.719
LIT 400kV N0 2 CUBNEZAIS-MARQUIS (LE) | 17T000000021768N | RTE | CUBNEZAIS | MARQUIS (LE) | 400 | 2374 | 2522 | 2522 | 2624 | [5 empty] | 0.371 | 3.923 | 47.398 | 63.062
LIT 400kV N0 2 CUBNEZAIS-SAUCATS | 17T000000021769L | RTE | CUBNEZAIS | SAUCATS | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.887 | 19.144 | 237.216 | 42.309
LIT 400kV N0 2 DAMBRON - GATINAIS | 17T000000022017Q | RTE | DAMBRON | GATINAIS | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.848 | 11.136 | 184.518 | 55.106
LIT 400kV N0 2 DAMBRON - VILLEJUST | 17T000000022019M | RTE | DAMBRON | VILLEJUST | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 2.138 | 21.707 | 267.882 | 59
LIT 400kV N0 2 DAMBRON-VERGER | 17T000000022018O | RTE | DAMBRON | VERGER | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 1.664 | 16.882 | 209.036 | 73.751
LIT 400kV N0 2 DISTRE - JUMEAUX (LES) | 17T000000022288W | RTE | DISTRE | JUMEAUX (LES) | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.394 | 14.142 | 175.286 | 70.591
LIT 400kV N0 2 DOMLOUP - LAUNAY | 17T0000000223629 | RTE | DOMLOUP | LAUNAY | 400 | 2494 | 2676 | 2676 | 2778 | [5 empty] | 1.412 | 18.552 | 307.644 | 48.525
LIT 400kV N0 2 DOMLOUP - LOUISFERT (poste F) | 17T0000000223637 | RTE | DOMLOUP | LOUISFERT | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.469 | 14.91 | 184.07 | 43.888
LIT 400kV N0 2 DOMLOUP - OUDON | 17T0000000223645 | RTE | DOMLOUP | OUDON | 400 | 3255 | 3600 | 3600 | 3780 | [5 empty] | 0.95 | 12.008 | 197.684 | 49.674
LIT 400kV N0 2 DONZAC-VERFEIL | 17T000000022402N | RTE | DONZAC | VERFEIL | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.797 | 23.746 | 391.394 | 16.746
LIT 400kV N0 2 ECHALAS-PIVOZ-CORDIER | 17T0000000226083 | RTE | ECHALAS | PIVOZ-CORDIER | 400 | 2170 | 2300 | 2300 | 2400 | [5 empty] | 0.268 | 4.901 | 65.582 | 88.692
LIT 400kV N0 2 EGUZON-VALDIVIENNE | 17T000000022698D | RTE | EGUZON | VALDIVIENNE | 400 | 1600 | 1772 | 1772 | 1904 | [5 empty] | 1.517 | 19.973 | 331.642 | 22.401
LIT 400kV N0 2 GATINAIS - GAUGLIN | 17T0000000239677 | RTE | GATINAIS | GAUGLIN | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.752 | 22.99 | 380.86 | 44.839
LIT 400kV N0 2 GATINAIS - TABARDERIE | 17T0000000239685 | RTE | GATINAIS | TABARDERIE | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.899 | 11.804 | 195.63 | 59.272
LIT 400kV N0 2 GAUGLIN-ST-ELOI | 17T000000024024J | RTE | GAUGLIN | ST-ELOI | 400 | 2200 | 2556 | 2556 | 2800 | [5 empty] | 1.417 | 18.639 | 309.22 | 70.839
LIT 400kV N0 2 GENISSIAT-POSTE-VIELMOULIN | 17T000000024078X | RTE | GENISSIAT-POSTE | VIELMOULIN | 400 | 1236 | 1236 | 1236 | 1236 | [5 empty] | 3.537 | 51.373 | 640.226 | 2.342
LIT 400kV N0 2 GRANZAY - JUMEAUX (LES) | 17T000000024402D | RTE | GRANZAY | JUMEAUX (LES) | 400 | 3072 | 3414 | 3414 | 3598 | [5 empty] | 2.364 | 24.317 | 301.454 | 64.873
LIT 400kV N0 2 GRANZAY - PREGUILLAC | 17T000000024403B | RTE | GRANZAY | PREGUILLAC | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.349 | 19.588 | 243.974 | 103.445
LIT 400kV N0 2 GRANZAY - VALDIVIENNE | 17T0000000244049 | RTE | GRANZAY | VALDIVIENNE | 400 | 2238 | 2382 | 2382 | 2526 | [5 empty] | 2.069 | 27.226 | 451.594 | 114.7
LIT 400kV N0 2 HAVRE (LE) (POSTE) - ROUGEMONTIER | 17T0000000247769 | RTE | HAVRE (LE) (POSTE) | ROUGEMONTIER | 400 | 2104 | 2300 | 2300 | 2400 | [5 empty] | 1.685 | 17.036 | 198.536 | 54.154
LIT 400kV N0 2 HOUDREVILLE-MERY-SUR-SEINE | 17T-FR-00000020C | RTE | HOUDREVILLE | MERY-SUR-SEINE | 400 | 2170 | 2400 | 2400 | 2574 | [5 empty] | 4.883 | 49.523 | 613.692 | 38.918
LIT 400kV N0 2 ISSEL - VERFEIL | 17T000000025010P | RTE | ISSEL | VERFEIL | 400 | 2462 | 2644 | 2644 | 2798 | [5 empty] | 1.169 | 11.866 | 146.582 | 25.681
LIT 400kV N0 2 LA GAUDIERE - ISSEL | 17T000000023981D | RTE | GAUDIERE (LA) | ISSEL | 400 | 3150 | 3392 | 3392 | 3590 | [5 empty] | 1.776 | 18.018 | 222.828 | 97.047
LIT 400kV N0 2 LA GAUDIERE - TAMAREAU | 17T000000024022N | RTE | GAUDIERE (LA) | TAMAREAU | 400 | 3195 | 3561 | 3561 | 3780 | [5 empty] | 2.036 | 28.774 | 378.328 | 70.83
LIT 400kV N0 2 LAUNAY-TAUTE | 17T000000025594A | RTE | LAUNAY | TAUTE | 400 | 3255 | 3600 | 3600 | 3780 | [5 empty] | 1.641 | 21.579 | 358.302 | 40.283
LIT 400kV N0 2 LONNY-MASTAING | 17T-FR-000000236 | RTE | LONNY | MASTAING | 400 | 2196 | 2400 | 2400 | 2596 | [5 empty] | 2.374 | 31.112 | 515.832 | 10.831
LIT 400kV N0 2 LONNY-MAZURES | 17T000000025950E | RTE | LONNY | MAZURES | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.325 | 3.339 | 40.41 | 10.831
LIT 400kV N0 2 LONNY-MOULAINE | 17T-FR-000000244 | RTE | LONNY | MOULAINE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 2.259 | 29.692 | 491.154 | 118.211
LIT 400kV N0 2 MARMAGNE-TABARDERIE | 17T000000026462M | RTE | MARMAGNE | TABARDERIE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 2.791 | 30.898 | 308.078 | 36
LIT 400kV N0 2 MENUEL-TAUTE | 17T000000026663C | RTE | MENUEL | TAUTE | 400 | 2662 | 2878 | 2878 | 2996 | [5 empty] | 0.729 | 9.584 | 159.126 | 14.3
LIT 400kV N0 2 MENUEL-TOLLEVAST | 17T000000026664A | RTE | MENUEL | TOLLEVAST | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.429 | 4.347 | 53.954 | 36
LIT 400kV N0 2 MERY-SUR-SEINE-VIELMOULIN | 17T000000026170Z | RTE | MERY-SUR-SEINE | VIELMOULIN | 400 | 2070 | 2282 | 2282 | 2400 | [5 empty] | 3.147 | 45.696 | 569.418 | 80.781
LIT 400kV N0 2 MEZEROLLES - TILLEUL | 17T000000026735D | RTE | MEZEROLLES | TILLEUL | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 2.106 | 21.35 | 264.58 | 58.72
LIT 400kV N0 2 MEZEROLLES - VILLEJUST | 17T000000026736B | RTE | MEZEROLLES | VILLEJUST | 400 | 3780 | 3780 | 3780 | 4095 | [5 empty] | 1.802 | 18.299 | 225.95 | 54.911
LIT 400kV N0 2 MORBRAS - VILLEVAUDE | 17T000000026947Z | RTE | MORBRAS | VILLEVAUDE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.233 | 3.897 | 67.962 | 15.218
LIT 400kV N0 2 MOULAINE-VIGY | 17T-FR-000000309 | RTE | MOULAINE | VIGY | 400 | 2070 | 2272 | 2272 | 2410 | [5 empty] | 1.233 | 16.21 | 268.834 | 52.745
LIT 400kV N0 2 MUHLBACH-SIERENTZ | 17T-FR-000000333 | RTE | MUHLBACH | SIERENTZ | 400 | 2202 | 2425 | 2426 | 2598 | [5 empty] | 1.3 | 10.7 | 89.4 | 0.3
LIT 400kV N0 2 NEOULES - TRANS | 17T0000000273972 | RTE | NEOULES | TRANS | 400 | 2128 | 2326 | 2326 | 2482 | [5 empty] | 1.357 | 13.765 | 170.198 | 45.11
LIT 400kV N0 2 NEOULES-REALTOR | 17T0000000273964 | RTE | NEOULES | REALTOR | 400 | 2006 | 2192 | 2192 | 2336 | [5 empty] | 2.16 | 20.427 | 256.624 | 68.288
LIT 400kV N0 2 OUDON - TAUTE | 17T000000027601T | RTE | OUDON | TAUTE | 400 | 3900 | 4050 | 4050 | 4200 | [5 empty] | 3.26 | 42.869 | 711.79 | 163
LIT 400kV N0 2 PLESSIS-GASSOT - TERRIER | 17T000000027710O | RTE | PLESSIS-GASSOT | TERRIER | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.802 | 8.904 | 110.416 | 29.093
LIT 400kV N0 2 PRAZ-ST-ANDRE - PIQUAGE A LA PRAZ-ST-ANDRE | 17T000000935461Y | RTE | PRAZ-ST-ANDRE | PIQUAGE A LA PRAZ-ST-ANDRE | 400 | 2585 | 2633 | 2633 | 2715 | [5 empty] | 0.003 | 0.049 | 0.606 | 0.138
LIT 400kV N0 2 REALTOR - TAVEL | 17T0000000285385 | RTE | REALTOR | TAVEL | 400 | 2128 | 2326 | 2326 | 2482 | [5 empty] | 2.731 | 27.719 | 343.574 | 91.947
LIT 400kV N0 2 REMISE - TERRIER | 17T000000028602M | RTE | REMISE | TERRIER | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.576 | 7.568 | 125.29 | 28.73
LIT 400kV N0 2 ROUGEMONTIER - TOURBE | 17T000000028769N | RTE | ROUGEMONTIER | TOURBE | 400 | 3416 | 3622 | 3622 | 3780 | [5 empty] | 1.735 | 25.184 | 314.154 | 83.032
LIT 400kV N0 2 ROUGEMONTIER-TILLEUL | 17T000000028768P | RTE | ROUGEMONTIER | TILLEUL | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 1.192 | 12.086 | 149.636 | 41.201
LIT 400kV N0 2 TAMAREAU - TAVEL | 17T000000029340L | RTE | TAMAREAU | TAVEL | 400 | 4400 | 4500 | 4500 | 4500 | [5 empty] | 2.009 | 28.503 | 338.61 | 91
LIT 400kV N0 2 TAUTE-TERRETTE | 17T000000029362B | RTE | TAUTE | TERRETTE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.28 | 3.682 | 61.136 | 13.998
LIT 400kV N0 2 TAVEL - TRICASTIN-POSTE (LE) | 17T000000029369Y | RTE | TAVEL | TRICASTIN-POSTE (LE) | 400 | 2212 | 2380 | 2380 | 2498 | [5 empty] | 1.294 | 12.506 | 155.668 | 41.878
LIT 400kV N0 2 TERRETTE - TOURBE | 17T000000029378X | RTE | TERRETTE | TOURBE | 400 | 3416 | 3622 | 3622 | 3780 | [5 empty] | 1.469 | 21.342 | 265.774 | 69.974
LIT 400kV N0 2 VERGER - VILLERBON | 17T000000029533A | RTE | VERGER | VILLERBON | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.806 | 8.182 | 101.058 | 26.822
LIT 400kV N0 3 ALBERTVILLE - GRANDE-ILE | 17T-FR-00000064T | RTE | ALBERTVILLE | GRANDE-ILE | 400 | 1926 | 2112 | 2112 | 2178 | [5 empty] | 1.665 | 18.949 | 127.516 | 44.337
LIT 400kV N0 3 ARGOEUVES - TERRIER | 17T0000000159835 | RTE | ARGOEUVES | TERRIER | 400 | 1514 | 1794 | 1794 | 2100 | [5 empty] | 2.634 | 25.809 | 298.776 | 81.806
LIT 400kV N0 3 BRAUD - CUBNEZAIS | 17T000000018505Q | RTE | BRAUD | CUBNEZAIS | 400 | 3072 | 3414 | 3414 | 3598 | [5 empty] | 0.673 | 9.771 | 121.516 | 32.014
LIT 400kV N0 3 CANTEGRIT - SAUCATS | 17T-FR-000000414 | RTE | CANTEGRIT | SAUCATS | 400 | 2690 | 2822 | 2822 | 2936 | [5 empty] | 1.942 | 25.172 | 239.5 | 71.813
LIT 400kV N0 3 CHAFFARD (LE) - ST-VULBAS-OUEST | 17T000000020029T | RTE | CHAFFARD (LE) | ST-VULBAS-OUEST | 400 | 2300 | 2400 | 2400 | 2400 | [5 empty] | 0.569 | 5.784 | 71.286 | 18.945
LIT 400kV N0 3 CHESNOY (LE) - TABARDERIE | 17T000000020447B | RTE | CHESNOY (LE) | TABARDERIE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 1.838 | 26.463 | 334.574 | 29.657
LIT 400kV N0 3 CIROLLIERS-VILLEJUST | 17T000000020618A | RTE | CIROLLIERS | VILLEJUST | 400 | 1850 | 2194 | 2194 | 2370 | [5 empty] | 0.928 | 7.271 | 76.506 | 21.49
LIT 400kV N0 3 COULANGE - TRICASTIN-POSTE (LE) | 17T000000021299W | RTE | COULANGE | TRICASTIN-POSTE (LE) | 400 | 2600 | 2700 | 2700 | 2800 | [5 empty] | 1.404 | 13.77 | 171.78 | 30.772
LIT 400kV N0 3 GENISSIAT-POSTE - VIELMOULIN | 17T000000024079V | RTE | GENISSIAT-POSTE | VIELMOULIN | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 7.59 | 58.345 | 567.492 | 79.944
LIT 400kV N0 3 HAVRE (LE) (POSTE) - ROUGEMONTIER | 17T0000000247777 | RTE | HAVRE (LE) (POSTE) | ROUGEMONTIER | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 1.684 | 17.027 | 198.43 | 40.976
LIT 400kV N0 3 LONNY-MASTAING | 17T-FR-000000252 | RTE | LONNY | MASTAING | 400 | 2366 | 2596 | 2596 | 2778 | [5 empty] | 2.361 | 31.053 | 515.602 | 80.779
LIT 400kV N0 3 MENUEL-TAUTE | 17T0000000266658 | RTE | MENUEL | TAUTE | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.72 | 9.468 | 157.206 | 36.17
LIT 400kV N0 3 PLESSIS-GASSOT - TERRIER | 17T000000027711M | RTE | PLESSIS-GASSOT | TERRIER | 400 | 3465 | 3622 | 3622 | 3780 | [5 empty] | 0.551 | 7.223 | 119.13 | 27.362
LIT 400kV N0 3 TAVEL - TRICASTIN-POSTE (LE) | 17T000000029370C | RTE | TAVEL | TRICASTIN-POSTE (LE) | 400 | 2334 | 2470 | 2470 | 2596 | [5 empty] | 1.686 | 15.385 | 204.148 | 51.028
LIT 400kV N0 4 BRAUD - CUBNEZAIS | 17T000000018506O | RTE | BRAUD | CUBNEZAIS | 400 | 3072 | 3414 | 3414 | 3598 | [5 empty] | 0.674 | 9.78 | 121.63 | 32.045
LIT 400kV N0 4 CHAFFARD (LE) - ST-VULBAS-OUEST | 17T0000000200307 | RTE | CHAFFARD (LE) | ST-VULBAS-OUEST | 400 | 2300 | 2450 | 2450 | 2600 | [5 empty] | 0.569 | 5.778 | 71.23 | 20.979
LIT 400kV N0 4 MENUEL-TAUTE | 17T0000000266666 | RTE | MENUEL | TAUTE | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.72 | 9.468 | 157.206 | 70.763
LIT 400kV N0 4 PLESSIS-GASSOT - TERRIER | 17T000000027712K | RTE | PLESSIS-GASSOT | TERRIER | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.552 | 7.225 | 119.176 | 27.372
LIT 400kV N0 4 PLESSIS-GASSOT - VILLEVAUDE | 17T000000027713I | RTE | PLESSIS-GASSOT | VILLEVAUDE | 400 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.785 | 8.731 | 85.616 | 25.401
LIT 400kV N0 4 TAVEL - TRICASTIN-POSTE (LE) | 17T000000029371A | RTE | TAVEL | TRICASTIN-POSTE (LE) | 400 | 3900 | 4050 | 4050 | 4200 | [5 empty] | 0.589 | 10.034 | 174.418 | 39.048
LIT 400kV N0 5 TAVEL - TRICASTIN-POSTE (LE) | 17T0000000293728 | RTE | TAVEL | TRICASTIN-POSTE (LE) | 400 | 3900 | 4050 | 4050 | 4200 | [5 empty] | 0.589 | 10.025 | 174.256 | 39.045
LIT 225kV N0 1 AIRVAULT-BONNEAU | 17T000000015268T | RTE | AIRVAULT | BONNEAU | 220 | 932 | 932 | 1145 | 1145 | [5 empty] | 3.064 | 20.35 | 239.62 | 52.792
LIT 225kV N0 1 AIRVAULT-JUMEAUX (LES) | 17T000000015269R | RTE | AIRVAULT | JUMEAUX (LES) | 220 | 1249 | 1337 | 1337 | 1434 | [5 empty] | 0.33 | 2.212 | 15.866 | 5.507
LIT 225kV N0 1 ALBERTVILLE-CHAVANOD | 17T-FR-00000048R | RTE | ALBERTVILLE | CHAVANOD | 220 | 617 | 685 | 685 | 742 | [5 empty] | 4.46 | 17.21 | 120 | 42.135
LIT 225kV N0 1 ALBERTVILLE-CONTAMINE | 17T000000015311H | RTE | ALBERTVILLE | CONTAMINE | 220 | 565 | 673 | 673 | 765 | [5 empty] | 2.352 | 10.043 | 70.716 | 24.925
LIT 225kV N0 1 ALBERTVILLE-LONGEFAN | 17T000000015312F | RTE | ALBERTVILLE | LONGEFAN | 220 | 565 | 673 | 673 | 765 | [5 empty] | 4.486 | 17.749 | 122.892 | 43.669
LIT 225kV N0 1 ALBERTVILLE-MALGOVERT | 17T000000015313D | RTE | ALBERTVILLE | MALGOVERT | 220 | 565 | 673 | 673 | 765 | [5 empty] | 3.54 | 16.64 | 110 | 40.633
LIT 225kV N0 1 ALBERTVILLE-VENTHON-POSTE | 17T0000000153159 | RTE | ALBERTVILLE | VENTHON-POSTE | 220 | 231 | 468 | 468 | 611 | [5 empty] | 0.39 | 1.58 | 10 | 3.79
LIT 225kV N0 1 ALLINGES-CORNIER | 17T000000015397I | RTE | ALLINGES | CORNIER | 220 | 966 | 1076 | 1076 | 1168 | [5 empty] | 2.42 | 14.488 | 107.984 | 36.996
LIT 225kV N0 1 ANOULD-ETIVAL | 17T0000000157103 | RTE | ANOULD | ETIVAL | 220 | 1070 | 1155 | 1155 | 1265 | [5 empty] | 2.888 | 19.202 | 136.054 | 47.62
LIT 225kV N0 1 AOSTE-BISSY | 17T000000015750S | RTE | AOSTE | BISSY | 220 | 236 | 470 | 470 | 612 | [5 empty] | 2.398 | 10.316 | 66.82 | 24.49
LIT 225kV N0 1 AQUEDUCS (LES)-CIROLLIERS | 17T0000000157859 | RTE | AQUEDUCS (LES) | CIROLLIERS | 220 | 827 | 1015 | 1015 | 1150 | [5 empty] | 0.549 | 3.644 | 26.52 | 9.163
LIT 225kV N0 1 ARDOISE (L )-MOTTE (LA) (VILLENEUVE-LES-AVIGNON | 17T000000015865B | RTE | ARDOISE (L ) | MOTTE (LA) (VILLENEUVE-LES-AVIGNON) | 220 | 1025 | 1025 | 1200 | 1200 | [5 empty] | 0.933 | 5.916 | 150.93 | 15.768
LIT 225kV N0 1 ARDOISE (L )-TAVEL | 17T0000000158677 | RTE | ARDOISE (L ) | TAVEL | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 0.649 | 4.346 | 31.182 | 10.819
LIT 225kV N0 1 ARENC-BELLE-DE-MAI | 17T000000015873C | RTE | ARENC | BELLE-DE-MAI | 220 | 510 | 510 | 640 | 640 | [5 empty] | 0.251 | 0.483 | 140.516 | 2.88
LIT 225kV N0 1 ARGIESANS-ETUPES | 17T000000015942J | RTE | ARGIESANS | ETUPES | 220 | 654 | 758 | 758 | 857 | [5 empty] | 0.867 | 4.44 | 31.282 | 11.145
LIT 225kV N0 1 ARGIESANS-SIERENTZ | 17T000000015943H | RTE | ARGIESANS | SIERENTZ | 220 | 654 | 758 | 758 | 857 | [5 empty] | 4.645 | 21.857 | 151.878 | 54.5
LIT 225kV N0 1 ARGOEUVES - BRAILLY-CORNEHOTTE | 17T000000015951I | RTE | ARGOEUVES | BRAILLY-CORNEHOTTE | 220 | 894 | 944 | 944 | 1017 | [5 empty] | 3.497 | 15.821 | 109.104 | 38.875
LIT 225kV N0 1 ARGOEUVES-BEAUCHAMPS | 17T000000015953E | RTE | ARGOEUVES | BEAUCHAMPS | 220 | 753 | 925 | 925 | 1075 | [5 empty] | 3.214 | 21.636 | 155.084 | 54.086
LIT 225kV N0 1 ARGOEUVES-BLOCAUX | 17T000000015952G | RTE | ARGOEUVES | BLOCAUX | 220 | 1250 | 1250 | 1250 | 1250 | [5 empty] | 2.47 | 16.435 | 118.874 | 41.056
LIT 225kV N0 1 ARLOD-GENISSIAT-POSTE | 17T000000016024F | RTE | ARLOD | GENISSIAT-POSTE | 220 | 557 | 557 | 653 | 653 | [5 empty] | 0.34 | 1.76 | 72 | 5.279
LIT 225kV N0 1 ARNAGE-QUINTES (LES) | 17T0000000160708 | RTE | ARNAGE | QUINTES (LES) | 220 | 1249 | 1316 | 1316 | 1389 | [5 empty] | 0.336 | 2.231 | 16.236 | 5.605
LIT 225KV N0 1 ARRIGHI - CHEVILLY | 17T0000000161615 | RTE | ARRIGHI | CHEVILLY | 220 | 888 | 910 | 972 | 1049 | [5 empty] | 0.962 | 5.29 | 168.574 | 14.029
LIT 225kV N0 1 ARRIGHI-CHARENTON | 17T0000000161607 | RTE | ARRIGHI | CHARENTON | 220 | 220 | 220 | 340 | 340 | [5 empty] | 0.137 | 0.47 | 408.442 | 4.511
LIT 225kV N0 1 ARRIGHI-MORBRAS | 17T000000016185S | RTE | ARRIGHI | MORBRAS | 220 | 2008 | 2008 | 2300 | 2400 | [5 empty] | 0.67 | 6.3 | 133.74 | 22.138
LIT 225kV N0 1 ARRIGHI-VILLENEUVE-ST-GEORGES | 17T000000016187O | RTE | ARRIGHI | VILLENEUVE-ST-GEORGES | 220 | 750 | 750 | 830 | 830 | [5 empty] | 0.42 | 2.62 | 40.62 | 6.719
LIT 225kV N0 1 ATTAQUES (LES)-ECHINGHEN | 17T000000016281W | RTE | ATTAQUES (LES) | ECHINGHEN | 220 | 1002 | 1078 | 1078 | 1130 | [5 empty] | 2.375 | 14.294 | 102.35 | 36.192
LIT 225kV N0 1 ATTAQUES (LES)-MANDARINS | 17T000000016302D | RTE | ATTAQUES (LES) | MANDARINS | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 0.607 | 4.047 | 29.266 | 10.125
LIT 225kV N0 1 AUBE-COMMERVEIL | 17T000000016320B | RTE | AUBE | COMMERVEIL | 220 | 938 | 987 | 987 | 1041 | [5 empty] | 4.993 | 22.672 | 152.262 | 54.801
LIT 225kV N0 1 AUBE-MEZEROLLES | 17T0000000163219 | RTE | AUBE | MEZEROLLES | 220 | 731 | 835 | 835 | 930 | [5 empty] | 8.662 | 39.653 | 274.442 | 97.448
LIT 225kV N0 1 AUBUSSON-EGUZON | 17T000000016387G | RTE | AUBUSSON | EGUZON | 220 | 894 | 991 | 991 | 1051 | [5 empty] | 6.57 | 30.04 | 198 | 73.228
LIT 225kV N0 1 AUBUSSON-MOLE (LA) | 17T000000016388E | RTE | AUBUSSON | MOLE (LA) | 220 | 286 | 531 | 531 | 674 | [5 empty] | 6.061 | 28.674 | 186.626 | 68.298
LIT 225kV N0 1 AULNOYE-PONT-SUR-SAMBRE | 17T000000016428S | RTE | AULNOYE | PONT-SUR-SAMBRE | 220 | 975 | 1030 | 1030 | 1110 | [5 empty] | 0.534 | 2.448 | 16.338 | 5.897
LIT 225kV N0 1 AUSSOIS-PRAZ-ST-ANDRE | 17T000000016508U | RTE | AUSSOIS | PRAZ-ST-ANDRE | 220 | 737 | 820 | 820 | 889 | [5 empty] | 1.07 | 4.33 | 30 | 10.429
LIT 225kV N0 1 AUZAT-TARASCON | 17T000000016551T | RTE | AUZAT | TARASCON | 220 | 737 | 820 | 820 | 889 | [5 empty] | 1.64 | 6.387 | 44.49 | 15.767
LIT 225kV N0 1 AVALLON - JOUX-LA-VILLE | 17T000000016555L | RTE | AVALLON | JOUX-LA-VILLE | 220 | 827 | 891 | 891 | 976 | [5 empty] | 1.543 | 7.83 | 53.35 | 19.039
LIT 225kV N0 1 AVELIN - MASTAING | 17T-FR-00000001G | RTE | AVELIN | MASTAING | 220 | 1273 | 1346 | 1346 | 1453 | [5 empty] | 0.938 | 10.277 | 110.114 | 31.508
LIT 225kV N0 1 AVELIN-COURRIERES | 17T000000016558F | RTE | AVELIN | COURRIERES | 220 | 1273 | 1346 | 1346 | 1451 | [5 empty] | 1.086 | 7.461 | 54.868 | 18.895
LIT 225kV N0 1 AVIGNON (POSTE)-CHATEAURENARD | 17T000000016626O | RTE | AVIGNON (POSTE) | CHATEAURENARD | 220 | 1198 | 1281 | 1281 | 1348 | [5 empty] | 0.663 | 4.41 | 30.75 | 10.858
LIT 225kV N0 1 AVIGNON (POSTE)-MOTTE (LA) (VILLENEUVE-LES-AVIG | 17T000000016627M | RTE | AVIGNON (POSTE) | MOTTE (LA) (VILLENEUVE-LES-AVIGNON) | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 0.355 | 2.363 | 17.082 | 5.86
LIT 225kV N0 1 AVOINE-AVOINE (POSTE 400 KV) | 17T000000016665E | RTE | AVOINE | AVOINE (POSTE 400 KV) | 220 | 1950 | 2025 | 2025 | 2100 | [5 empty] | 0.042 | 0.275 | 92.742 | 1.66
LIT 225kV N0 1 AVOINE-DISTRE | 17T000000016667A | RTE | AVOINE | DISTRE | 220 | 915 | 915 | 1075 | 1075 | [5 empty] | 1.294 | 8.775 | 158.758 | 23.105
LIT 225kV N0 1 AVOINE-QUINTES (LES) | 17T0000000166688 | RTE | AVOINE | QUINTES (LES) | 220 | 1100 | 1186 | 1186 | 1275 | [5 empty] | 4.462 | 30.705 | 226.828 | 78.477
LIT 225kV N0 1 BACALAN-BRUGES | 17T0000000170258 | RTE | BACALAN | BRUGES | 220 | 655 | 655 | 760 | 760 | [5 empty] | 0.593 | 3.97 | 32.794 | 9.894
LIT 225kV N0 1 BACALAN-MARQUIS (LE) | 17T0000000170266 | RTE | BACALAN | MARQUIS (LE) | 220 | 898 | 920 | 1030 | 1030 | [5 empty] | 1.12 | 7.583 | 76.562 | 19.408
LIT 225kV N0 1 BALARUC - FLORENSAC | 17T0000000171092 | RTE | BALARUC | FLORENSAC | 220 | 1161 | 1241 | 1241 | 1306 | [5 empty] | 1.562 | 10.27 | 73.614 | 34.393
LIT 225kV N0 1 BALARUC - MONTPELLIER | 17T000000017110H | RTE | BALARUC | MONTPELLIER | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 1.217 | 8.115 | 58.518 | 19.922
LIT 225kV N0 1 BALMA (POSTE)-VERFEIL | 17T000000017146X | RTE | BALMA (POSTE) | VERFEIL | 220 | 1080 | 1185 | 1185 | 1289 | [5 empty] | 0.945 | 6.329 | 45.326 | 28.277
LIT 225kV N0 1 BARBUISE - CRENEY | 17T000000017194M | RTE | BARBUISE | CRENEY | 220 | 684 | 781 | 781 | 869 | [5 empty] | 5.296 | 24.684 | 163.784 | 26.238
LIT 225kV N0 1 BARBUISE - FOSSES (LES) | 17T000000017195K | RTE | BARBUISE | FOSSES (LES) | 220 | 684 | 781 | 781 | 869 | [5 empty] | 4.727 | 22.104 | 148.894 | 39.31
LIT 225kV N0 1 BARJAC-CROISIERE | 17T0000000172226 | RTE | BARJAC | CROISIERE | 220 | 660 | 694 | 694 | 756 | [5 empty] | 4.819 | 15.387 | 118.666 | 21.472
LIT 225kV N0 1 BASTILLAC-LANNEMEZAN | 17T000000017307Z | RTE | BASTILLAC | LANNEMEZAN | 220 | 855 | 940 | 940 | 1025 | [5 empty] | 3.166 | 20.675 | 148.13 | 32.175
LIT 225kV N0 1 BATZENDORF-MARLENHEIM | 17T000000017343V | RTE | BATZENDORF | MARLENHEIM | 220 | 1100 | 1187 | 1187 | 1302 | [5 empty] | 1.804 | 11.989 | 87.04 | 11.884
LIT 225kV N0 1 BAYET - MONTVICQ | 17T000000017393G | RTE | BAYET | MONTVICQ | 220 | 814 | 855 | 983 | 1000 | [5 empty] | 2.11 | 14.64 | 118 | 92.259
LIT 225kV N0 1 BAYET-SEMINAIRE | 17T000000017394E | RTE | BAYET | SEMINAIRE | 220 | 358 | 692 | 692 | 883 | [5 empty] | 2.474 | 16.472 | 119.154 | 24.72
LIT 225kV N0 1 BAYET-VOLVIC | 17T000000017395C | RTE | BAYET | VOLVIC | 220 | 814 | 983 | 983 | 1099 | [5 empty] | 2.68 | 18.73 | 132 | 34.72
LIT 225kV N0 1 BEAULIEU-FARRADIERE (LA) | 17T0000000189521 | RTE | BEAULIEU | FARRADIERE (LA) | 220 | 632 | 890 | 890 | 1039 | [5 empty] | 1.799 | 12.415 | 91.578 | 16
LIT 225kV N0 1 BEAULIEU-GRANZAY | 17T000000018954Y | RTE | BEAULIEU | GRANZAY | 220 | 1249 | 1337 | 1337 | 1434 | [5 empty] | 3.287 | 21.903 | 158.488 | 28
LIT 225kV N0 1 BEAULIEU-SIRMIERE | 17T000000018955W | RTE | BEAULIEU | SIRMIERE | 220 | 1249 | 1337 | 1337 | 1432 | [5 empty] | 4.007 | 27.335 | 200.912 | 43.185
LIT 225kV N0 1 BEAUMONT-MONTEUX-VALENCE | 17T000000016942E | RTE | BEAUMONT-MONTEUX | VALENCE | 220 | 695 | 782 | 782 | 855 | [5 empty] | 1.17 | 5.76 | 46 | 11.268
LIT 225kV N0 1 BEAUREGARD (SAINT-LAURENT-NOUAN)-CHAINGY | 17T000000018976O | RTE | BEAUREGARD (SAINT-LAURENT-NOUAN) | CHAINGY | 220 | 483 | 675 | 675 | 786 | [5 empty] | 1.785 | 8.515 | 55.478 | 77.914
LIT 225kV N0 1 BEAUTOR (POSTE) - HERIE-LA-VIEVILLE | 17T0000000190208 | RTE | BEAUTOR (POSTE) | HERIE-LA-VIEVILLE (LE) | 220 | 507 | 709 | 709 | 822 | [5 empty] | 2.796 | 12.61 | 87.382 | 27.764
LIT 225kV N0 1 BEAUTOR (POSTE)-LATENA | 17T000000019062T | RTE | BEAUTOR (POSTE) | LATENA | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 1.75 | 12.011 | 88.696 | 12.168
LIT 225kV N0 1 BEAUTOR (POSTE)-LONG-CHAMP (LE) | 17T0000000190216 | RTE | BEAUTOR (POSTE) | LONG-CHAMP (LE) | 220 | 731 | 835 | 835 | 930 | [5 empty] | 4.258 | 20.966 | 145.752 | 0.7
LIT 225kV N0 1 BEAUTOR (POSTE)-SETIER | 17T000000019063R | RTE | BEAUTOR (POSTE) | SETIER | 220 | 899 | 984 | 984 | 1061 | [5 empty] | 1.916 | 8.609 | 59.79 | 32.825
LIT 225kV N0 1 BELLE-DE-MAI-ENCO-DE-BOTTE | 17T000000016905K | RTE | BELLE-DE-MAI | ENCO-DE-BOTTE | 220 | 610 | 610 | 705 | 705 | [5 empty] | 0.266 | 1.759 | 593.226 | 63.891
LIT 225kV N0 1 BELLE-EPINE - DOMLOUP | 17T000000016830P | RTE | BELLE-EPINE | DOMLOUP | 220 | 934 | 934 | 1154 | 1154 | [5 empty] | 1.018 | 6.863 | 151.06 | 7.202
LIT 225kV N0 1 BELLE-EPINE-RANCE-POSTE | 17T000000016831N | RTE | BELLE-EPINE | RANCE-POSTE | 220 | 795 | 864 | 864 | 931 | [5 empty] | 6.323 | 28.584 | 198.168 | 16.184
LIT 225kV N0 1 BERGE - CANTEGRIT | 17T000000017634K | RTE | BERGE | CANTEGRIT | 220 | 915 | 985 | 985 | 1060 | [5 empty] | 1.22 | 7.945 | 57.83 | 3.185
LIT 225kV N0 1 BERGE - MARSILLON | 17T000000017635I | RTE | BERGE | MARSILLON | 220 | 915 | 985 | 985 | 1060 | [5 empty] | 3.479 | 22.666 | 164.948 | 57.047
LIT 225kV N0 1 BERGHOLZ-MARLENHEIM | 17T000000017663D | RTE | BERGHOLZ | MARLENHEIM | 220 | 2200 | 2281 | 2281 | 2281 | [5 empty] | 0.767 | 11.003 | 172.4 | 41.359
LIT 225kV N0 1 BEZAUMONT-CROIX-DE-METZ | 17T000000017787W | RTE | BEZAUMONT | CROIX-DE-METZ | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 1.571 | 10.705 | 78.806 | 27.115
LIT 225kV N0 1 BEZAUMONT-CUSTINE | 17T000000017788U | RTE | BEZAUMONT | CUSTINE | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 0.761 | 5.07 | 36.64 | 12.619
LIT 225kV N0 1 BEZAUMONT-VANDIERES | 17T000000017789S | RTE | BEZAUMONT | VANDIERES | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 0.819 | 5.445 | 39.456 | 13.646
LIT 225KV N0 1 BEZIERS-EST - ST-VINCENT | 17T0000000177574 | RTE | BEZIERS-EST | ST-VINCENT | 220 | 419 | 419 | 419 | 567 | [5 empty] | 0.259 | 0.761 | 229.032 | 4.443
LIT 225kV N0 1 BEZON-PONTCHATEAU | 17T000000017825D | RTE | BEZON | PONTCHATEAU | 220 | 846 | 928 | 928 | 1005 | [5 empty] | 6.782 | 35.208 | 248.736 | 86.496
LIT 225kV N0 1 BEZON-POTEAU ROUGE | 17T000000017824F | RTE | BEZON | POTEAU-ROUGE | 220 | 983 | 1022 | 1022 | 1059 | [5 empty] | 6.829 | 35.619 | 251.492 | 88.449
LIT 225kV N0 1 BIANCON - FREJUS | 17T000000017831I | RTE | BIANCON | FREJUS | 220 | 1100 | 1100 | 1600 | 1600 | [5 empty] | 0.402 | 4.098 | 2250 | 24.588
LIT 225kV N0 1 BIANCON-MOUGINS | 17T000000017832G | RTE | BIANCON | MOUGINS | 220 | 1000 | 1000 | 1160 | 1185 | [5 empty] | 0.987 | 5.296 | 648.86 | 18.456
LIT 225kV N0 1 BIANCON-PLAN-DE-GRASSE | 17T000000017833E | RTE | BIANCON | PLAN-DE-GRASSE | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 0.705 | 5.149 | 527.966 | 17.853
LIT 225kV N0 1 BISSY-GRANDE-ILE | 17T000000017920J | RTE | BISSY | GRANDE-ILE | 220 | 566 | 672 | 672 | 764 | [5 empty] | 1.63 | 7.68 | 106.696 | 18.962
LIT 225kV N0 1 BLOCAUX - LIMEUX (400 kV) | 17T0000000180245 | RTE | BLOCAUX | LIMEUX | 220 | 967 | 967 | 1218 | 1218 | [5 empty] | 0.72 | 5.423 | 1889.02 | 29.137
LIT 225kV N0 1 BOISSE (LA) - CUSSET-POSTE | 17T0000000181055 | RTE | BOISSE (LA) | CUSSET-POSTE | 220 | 857 | 857 | 1024 | 1024 | [5 empty] | 0.66 | 4.98 | 74 | 12.613
LIT 225kV N0 1 BOISSE (LA) - GENISSIAT-POSTE | 17T0000000181063 | RTE | BOISSE (LA) | GENISSIAT-POSTE | 220 | 695 | 725 | 782 | 855 | [5 empty] | 6.206 | 27.41 | 208.858 | 68.301
LIT 225kV N0 1 BOISSE (LA) - ST-VULBAS-EST | 17T000000018110C | RTE | BOISSE (LA) | ST-VULBAS-EST | 220 | 900 | 1015 | 1015 | 1112 | [5 empty] | 1.263 | 8.463 | 60.67 | 21.057
LIT 225kV N0 1 BOLLENE-CHATEAUNEUF-DU-RHONE | 17T000000018155R | RTE | BOLLENE (POSTE RESEAU) | CHATEAUNEUF-DU-RHONE | 220 | 816 | 889 | 889 | 947 | [5 empty] | 1.996 | 10.196 | 100.992 | 24.939
LIT 225kV N0 1 BOLLENE-TERRADOU | 17T000000018158L | RTE | BOLLENE (POSTE RESEAU) | TERRADOU | 220 | 816 | 889 | 889 | 947 | [5 empty] | 3.767 | 17.664 | 123.036 | 43.937
LIT 225kV N0 1 BOLLENE-TRICASTIN-POSTE (LE) | 17T000000018159J | RTE | BOLLENE (POSTE RESEAU) | TRICASTIN-POSTE (LE) | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 0.325 | 2.172 | 15.584 | 5.56
LIT 225kV N0 1 BONNEAU-ORANGERIE (L) | 17T000000018195F | RTE | BONNEAU | ORANGERIE (L) | 220 | 1012 | 1150 | 1150 | 1247 | [5 empty] | 2.124 | 14.107 | 102.436 | 35.413
LIT 225kV N0 1 BONNEAU-VALDIVIENNE | 17T000000018196D | RTE | BONNEAU | VALDIVIENNE | 220 | 1180 | 1310 | 1310 | 1390 | [5 empty] | 1.656 | 10.454 | 84.73 | 27.611
LIT 225kV N0 1 BONNIERES - MEZEROLLES | 17T000000018237P | RTE | BONNIERES | MEZEROLLES | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 1.702 | 11.349 | 81.964 | 28.492
LIT 225kV N0 1 BOUDEYRE-CHATEAUNEUF-DU-RHONE | 17T000000018353N | RTE | BOUDEYRE | CHATEAUNEUF-DU-RHONE | 220 | 862 | 928 | 928 | 987 | [5 empty] | 2.433 | 11.463 | 80.012 | 28.383
LIT 225kV N0 1 BOUDEYRE-MONTPEZAT | 17T000000018354L | RTE | BOUDEYRE | MONTPEZAT | 220 | 862 | 928 | 928 | 987 | [5 empty] | 1.724 | 7.671 | 53.432 | 19.1
LIT 225kV N0 1 BOULE (LA) - PUTEAUX | 17T000000018391F | RTE | BOULE (LA) | PUTEAUX | 220 | 490 | 490 | 730 | 730 | [5 empty] | 0.091 | 0.613 | 285.84 | 3.507
LIT 225kV N0 1 BOURGUIGNON - ETUPES | 17T0000000191107 | RTE | BOURGUIGNON | ETUPES | 220 | 791 | 853 | 853 | 934 | [5 empty] | 1.431 | 5.598 | 38.924 | 13.832
LIT 225kV N0 1 BOURGUIGNON - MAMBELIN | 17T0000000191115 | RTE | BOURGUIGNON | MAMBELIN | 220 | 791 | 853 | 853 | 934 | [5 empty] | 1.143 | 4.789 | 33.694 | 11.881
LIT 225kV N0 1 BOUTRE - TRANS | 17T000000018431T | RTE | BOUTRE | TRANS | 220 | 1250 | 1250 | 1600 | 1600 | [5 empty] | 1.02 | 10.4 | 4902 | 64.661
LIT 225kV N0 1 BOUTRE-COUDON (LE) | 17T000000018427K | RTE | BOUTRE | COUDON (LE) | 220 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 1.641 | 17.352 | 263.256 | 63.4
LIT 225kV N0 1 BOUTRE-SAINTE-TULLE 1 | 17T000000018430V | RTE | BOUTRE | STE-TULLE | 220 | 1144 | 1249 | 1249 | 1333 | [5 empty] | 0.705 | 5.573 | 37.2 | 13.295
LIT 225kV N0 1 BRAILLY-CORNEHOTTE - SORRUS | 17T000000016790B | RTE | BRAILLY-CORNEHOTTE | SORRUS | 220 | 865 | 865 | 865 | 865 | [5 empty] | 2.769 | 12.603 | 87.356 | 30.947
LIT 225kV N0 1 BRENNILIS-MARTYRE (LA) | 17T000000018547A | RTE | BRENNILIS | MARTYRE (LA) | 220 | 1250 | 1312 | 1312 | 1375 | [5 empty] | 1.762 | 12.128 | 89.362 | 31.072
LIT 225kV N0 1 BRENNILIS-PLEYBER-CHRIST | 17T0000000185488 | RTE | BRENNILIS | PLEYBER-CHRIST | 220 | 1300 | 1350 | 1350 | 1400 | [5 empty] | 1.297 | 8.601 | 62.594 | 21.445
LIT 225kV N0 1 BRENS - PELISSIER | 17T000000018542K | RTE | BRENS (CNR) | PELISSIER | 220 | 831 | 984 | 984 | 1099 | [5 empty] | 0.979 | 6.546 | 47.5 | 16.576
LIT 225kV N0 1 BRENS - VERFEIL | 17T000000018543I | RTE | BRENS (CNR) | VERFEIL | 220 | 831 | 984 | 984 | 1099 | [5 empty] | 2.35 | 15.638 | 113.196 | 39.187
LIT 225kV N0 1 BREUIL (LE) - PIQUAGE A SAINT GERONS |  | RTE | BREUIL (LE) | PIQUAGE A SAINT GERONS | 220 | 629 | 756 | 756 | 844 | [5 empty] | 3.063 | 13.853 | 95.614 | 34.393
LIT 225kV N0 1 BREUIL (LE)-MOLE (LA) | 17T0000000185844 | RTE | BREUIL (LE) | MOLE (LA) | 220 | 622 | 748 | 748 | 834 | [5 empty] | 1.791 | 8.345 | 54.516 | 19.922
LIT 225kV N0 1 BREUIL (LE)-PEYRAT-LE-CHATEAU | 17T0000000185852 | RTE | BREUIL (LE) | PEYRAT-LE-CHATEAU | 220 | 629 | 756 | 756 | 844 | [5 empty] | 6.396 | 28.64 | 199.326 | 71.58
LIT 225kV N0 1 BROC-CARROS (LE) - LINGOSTIERE | 17T000000016754F | RTE | BROC-CARROS (LE) | LINGOSTIERE | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 0.69 | 4.616 | 33.122 | 11.971
LIT 225kV N0 1 BROC-CARROS (LE) - TRINITE-VICTOR | 17T000000016755D | RTE | BROC-CARROS (LE) | TRINITE-VICTOR | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 0.812 | 5.476 | 40.526 | 13.853
LIT 225kV N0 1 BRODE - PIQUAGE A DUVIGNEAU | 17T000000018641I | RTE | BRODE | PIQUAGE A DUVIGNEAU | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 0.023 | 0.155 | 1.11 | 0.368
LIT 225kV N0 1 BRUGES-PESSAC | 17T000000018716D | RTE | BRUGES | PESSAC | 220 | 655 | 655 | 760 | 760 | [5 empty] | 0.828 | 5.538 | 42.59 | 13.884
LIT 225kV N0 1 BUIRE-PONT-SUR-SAMBRE | 17T000000018795S | RTE | BUIRE | PONT-SUR-SAMBRE | 220 | 1250 | 1250 | 1250 | 1250 | [5 empty] | 2.641 | 17.72 | 126.416 | 44.04
LIT 225kV N0 1 BUTTES-CHAUMONT-ROMAINVILLE | 17T0000000167862 | RTE | BUTTES-CHAUMONT | ROMAINVILLE | 220 | 440 | 440 | 550 | 550 | [5 empty] | 0.17 | 0.66 | 574 | 6.198
LIT 225kV N0 1 CAEN - RANVILLE | 17T000000019441L | RTE | CAEN | RANVILLE | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 0.45 | 3.021 | 21.348 | 7.494
LIT 225kV N0 1 CALAN - POTEAU-ROUGE | 17T000000019479X | RTE | CALAN | POTEAU-ROUGE | 220 | 1110 | 1110 | 1403 | 1403 | [5 empty] | 0.104 | 1.067 | 508.946 | 6.8
LIT 225kV N0 1 CANTEGRIT-MARSILLON | 17T0000000195548 | RTE | CANTEGRIT | MARSILLON | 220 | 997 | 1096 | 1096 | 1155 | [5 empty] | 4.678 | 30.486 | 222.014 | 77.402
LIT 225kV N0 1 CANTEGRIT-MOUGUERRE | 17T-FR-00000063V | RTE | CANTEGRIT | MOUGUERRE | 220 | 1884 | 1890 | 1890 | 1890 | [5 empty] | 4.563 | 33.778 | 235.486 | 83.1
LIT 225kV N0 1 CANTEGRIT-NAOUTOT | 17T0000000195556 | RTE | CANTEGRIT | NAOUTOT | 220 | 935 | 1000 | 1000 | 1080 | [5 empty] | 2.296 | 15.425 | 108.942 | 38.208
LIT 225kV N0 1 CAPELLE (LA) - HERIE-LA-VIEVILLE | 17T000000019585Y | RTE | CAPELLE (LA) | HERIE-LA-VIEVILLE (LE) | 220 | 579 | 709 | 709 | 822 | [5 empty] | 2.985 | 14.747 | 103.352 | 33.829
LIT 225kV N0 1 CAPELLE (LA)-PONT-SUR-SAMBRE | 17T000000019586W | RTE | CAPELLE (LA) | PONT-SUR-SAMBRE | 220 | 1273 | 1346 | 1346 | 1453 | [5 empty] | 1.827 | 12.238 | 87.566 | 30.47
LIT 225kV N0 1 CARRIERES - PLESSIS-GASSOT | 17T000000019675X | RTE | CARRIERES | PLESSIS-GASSOT | 220 | 510 | 767 | 767 | 976 | [5 empty] | 1.622 | 10.781 | 76.648 | 26.831
LIT 225KV N0 1 CARRIERES - VALESCOURT | 17T000000019704F | RTE | CARRIERES | VALESCOURT | 220 | 1023 | 1161 | 1161 | 1266 | [5 empty] | 2.065 | 13.764 | 99.264 | 34.429
LIT 225kV N0 1 CARRIERES-MORU | 17T000000019674Z | RTE | CARRIERES | MORU | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 1.7 | 11.31 | 81.42 | 28.277
LIT 225kV N0 1 CARRIERES-TERRIER | 17T000000019676V | RTE | CARRIERES | TERRIER | 220 | 2046 | 2300 | 2300 | 2400 | [5 empty] | 0.469 | 4.417 | 63.648 | 15.649
LIT 225kV N0 1 CASTELLE (LA) - SAUMADE | 17T000000021657W | RTE | CASTELLE (LA) | SAUMADE | 220 | 745 | 775 | 932 | 940 | [5 empty] | 0.49 | 3.271 | 153.032 | 9.379
LIT 225kV N0 1 CASTELLE (LA) - TAMAREAU | 17T000000021658U | RTE | CASTELLE (LA) | TAMAREAU | 220 | 745 | 870 | 932 | 1010 | [5 empty] | 1.455 | 9.013 | 73.05 | 27.295
LIT 225kV N0 1 CASTELLET (LE) - ENCO-DE-BOTTE | 17T000000021682X | RTE | CASTELLET (LE) | ENCO-DE-BOTTE | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 1.344 | 8.918 | 64.906 | 22.408
LIT 225kV N0 1 CASTELLET (LE) - ESCAILLON (L ) | 17T000000021683V | RTE | CASTELLET (LE) | ESCAILLON (L ) | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 1.199 | 7.95 | 57.862 | 19.976
LIT 225kV N0 1 CAZARIL-JALIS | 17T000000019785Q | RTE | CAZARIL | JALIS | 220 | 828 | 908 | 908 | 986 | [5 empty] | 6.635 | 33.492 | 236.754 | 83.146
LIT 225kV N0 1 CAZARIL-LANNEMEZAN | 17T000000019786O | RTE | CAZARIL | LANNEMEZAN | 220 | 828 | 908 | 908 | 986 | [5 empty] | 1.054 | 5.037 | 33.138 | 12.123
LIT 225kV N0 1 CERGY - PLESSIS-GASSOT | 17T000000019863W | RTE | CERGY | PLESSIS-GASSOT | 220 | 520 | 782 | 782 | 998 | [5 empty] | 1.982 | 17.165 | 124.978 | 43.02
LIT 225kV N0 1 CERGY-PORCHEVILLE | 17T000000019864U | RTE | CERGY | PORCHEVILLE | 220 | 926 | 1060 | 1060 | 1181 | [5 empty] | 1.632 | 10.7 | 77.468 | 27.066
LIT 225kV N0 1 CERGY-PUISEUX | 17T000000019865S | RTE | CERGY | PUISEUX | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 0.28 | 1.865 | 13.508 | 4.67
LIT 225kV N0 1 CERNAY-VESLE | 17T0000000199047 | RTE | CERNAY | VESLE | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 1.051 | 7.006 | 50.622 | 17.55
LIT 225kV N0 1 CESTAS - MASQUET | 17T0000000199144 | RTE | CESTAS | MASQUET | 220 | 932 | 1049 | 1049 | 1126 | [5 empty] | 1.049 | 6.969 | 63.384 | 17.6
LIT 225kV N0 1 CESTAS - PESSAC | 17T0000000199152 | RTE | CESTAS | PESSAC | 220 | 932 | 1049 | 1049 | 1126 | [5 empty] | 0.842 | 5.602 | 55.454 | 14.472
LIT 225kV N0 1 CHABOSSIERE (LA)-CHEVIRE | 17T000000019982O | RTE | CHABOSSIERE (LA) | CHEVIRE | 220 | 1249 | 1337 | 1337 | 1432 | [5 empty] | 0.422 | 2.86 | 21.098 | 7.334
LIT 225kV N0 1 CHABOSSIERE (LA)-CORDEMAIS-POSTE | 17T000000019983M | RTE | CHABOSSIERE (LA) | CORDEMAIS-POSTE | 220 | 1249 | 1337 | 1337 | 1432 | [5 empty] | 1.114 | 7.536 | 55.842 | 19.522
LIT 225kV N0 1 CHAINGY-DAMBRON | 17T000000020068J | RTE | CHAINGY | DAMBRON | 220 | 888 | 983 | 983 | 1042 | [5 empty] | 1.572 | 10.561 | 74.586 | 26.338
LIT 225kV N0 1 CHALON-CHAMPVANS | 17T000000020108X | RTE | CHALON | CHAMPVANS | 220 | 641 | 742 | 742 | 836 | [5 empty] | 5.585 | 25.536 | 172.398 | 61.86
LIT 225kV N0 1 CHALON-GROSNE | 17T000000020109V | RTE | CHALON | GROSNE | 220 | 1400 | 1500 | 1500 | 1550 | [5 empty] | 0.752 | 7.047 | 102.744 | 25.08
LIT 225kV N0 1 CHAMPAGNIER-EYBENS | 17T000000021381A | RTE | CHAMPAGNIER | EYBENS | 220 | 1093 | 1178 | 1178 | 1253 | [5 empty] | 0.519 | 3.384 | 24.566 | 8.4
LIT 225kV N0 1 CHAMPAGNIER-GRISOLLES | 17T000000021402S | RTE | CHAMPAGNIER | GRISOLLES | 220 | 734 | 856 | 856 | 964 | [5 empty] | 5.011 | 32.529 | 261.52 | 82.181
LIT 225kV N0 1 CHAMPAGNIER-MOIRANS | 17T000000021403Q | RTE | CHAMPAGNIER | MOIRANS | 220 | 1123 | 1211 | 1211 | 1290 | [5 empty] | 1.075 | 11.551 | 127.326 | 35.406
LIT 225kV N0 1 CHAMPAGNIER-PARISET | 17T000000021404O | RTE | CHAMPAGNIER | PARISET | 220 | 570 | 659 | 659 | 739 | [5 empty] | 1.13 | 3.95 | 28 | 9.41
LIT 225kV N0 1 CHAMPAGNIER-SERRE-PONCON | 17T000000021406K | RTE | CHAMPAGNIER | SERRE-PONCON | 220 | 734 | 856 | 856 | 964 | [5 empty] | 5.92 | 39.82 | 300 | 98.635
LIT 225kV N0 1 CHAMPAGNOLE - FRASNE | 17T000000021418D | RTE | CHAMPAGNOLE | FRASNE | 220 | 801 | 930 | 930 | 1053 | [5 empty] | 1.637 | 9.735 | 72.336 | 24.838
LIT 225kV N0 1 CHAMPAGNOLE - SAONE | 17T000000021421O | RTE | CHAMPAGNOLE | SAONE | 220 | 455 | 555 | 555 | 632 | [5 empty] | 7.144 | 24.248 | 152.244 | 56.775
LIT 225kV N0 1 CHAMPAGNOLE-GENISSIAT-POSTE | 17T000000021419B | RTE | CHAMPAGNOLE | GENISSIAT-POSTE | 220 | 264 | 437 | 437 | 545 | [5 empty] | 11.011 | 36.498 | 227.824 | 85.139
LIT 225kV N0 1 CHAMPS-REGNAUD-VIELMOULIN | 17T000000019343L | RTE | CHAMPS-REGNAUD | VIELMOULIN | 220 | 843 | 909 | 909 | 996 | [5 empty] | 2.649 | 12.359 | 86.01 | 30.5
LIT 225kV N0 1 CHAMPVANS-PYMONT | 17T0000000214492 | RTE | CHAMPVANS | PYMONT | 220 | 751 | 923 | 923 | 1056 | [5 empty] | 2.767 | 19.099 | 140.878 | 48.515
LIT 225kV N0 1 CHATEAU-GOMBERT - ENCO-DE-BOTTE | 17T0000000192006 | RTE | CHATEAU-GOMBERT | ENCO-DE-BOTTE | 220 | 438 | 438 | 438 | 438 | [5 empty] | 0.337 | 1.122 | 343.364 | 6.355
LIT 225kV N0 1 CHATEAUNEUF-DU-RHONE - TRICASTIN-POSTE (LE) | 17T000000019357A | RTE | CHATEAUNEUF-DU-RHONE | TRICASTIN-POSTE (LE) | 220 | 862 | 928 | 928 | 987 | [5 empty] | 1.723 | 8.881 | 61.826 | 21.904
LIT 225kV N0 1 CHATEAUNEUF-DU-RHONE-LOGIS-NEUF | 17T000000019356C | RTE | CHATEAUNEUF-DU-RHONE | LOGIS-NEUF | 220 | 862 | 928 | 928 | 987 | [5 empty] | 2.693 | 12.205 | 83.676 | 30
LIT 225kV N0 1 CHAUSSEE (LA)-RECY | 17T000000021857O | RTE | CHAUSSEE (LA) | RECY | 220 | 1172 | 1268 | 1268 | 1355 | [5 empty] | 1.598 | 10.643 | 74.268 | 26.238
LIT 225kV N0 1 CHAUSSEE (LA)-REVIGNY | 17T000000021858M | RTE | CHAUSSEE (LA) | REVIGNY | 220 | 1140 | 1248 | 1248 | 1347 | [5 empty] | 2.335 | 15.545 | 107.632 | 38.162
LIT 225kV N0 1 CHAVANOD-GENISSIAT-POSTE | 17T-FR-00000049P | RTE | CHAVANOD | GENISSIAT-POSTE | 220 | 617 | 659 | 685 | 742 | [5 empty] | 4.69 | 16.11 | 112 | 39.113
LIT 225kV N0 1 CHESNOY (LE)-COURTRY | 17T000000020404T | RTE | CHESNOY (LE) | COURTRY | 220 | 899 | 984 | 984 | 1061 | [5 empty] | 1.747 | 8.063 | 56.416 | 19.948
LIT 225kV N0 1 CHESNOY (LE)-NEMOURS | 17T000000020406P | RTE | CHESNOY (LE) | NEMOURS | 220 | 520 | 782 | 782 | 998 | [5 empty] | 2.114 | 14.347 | 105.908 | 36.369
LIT 225kV N0 1 CHESNOY (LE)-ROUSSON | 17T000000020408L | RTE | CHESNOY (LE) | ROUSSON | 220 | 786 | 867 | 867 | 948 | [5 empty] | 4.082 | 18.523 | 178.76 | 45.817
LIT 225KV N0 1 CHEVILLY - VILLENEUVE-ST- | 17T000000020523L | RTE | CHEVILLY | VILLENEUVE-ST-GEORGES | 220 | 750 | 750 | 830 | 830 | [5 empty] | 0.63 | 3.118 | 29.58 | 7.503
LIT 225kV N0 1 CHEVILLY-CORIOLIS | 17T000000020499T | RTE | CHEVILLY | CORIOLIS | 220 | 425 | 425 | 540 | 540 | [5 empty] | 0.556 | 1.326 | 726.934 | 10.695
LIT 225kV N0 1 CHEVIRE-MERLATIERE | 17T0000000204594 | RTE | CHEVIRE | MERLATIERE | 220 | 1249 | 1337 | 1337 | 1432 | [5 empty] | 2.997 | 20.647 | 151.996 | 52.396
LIT 225kV N0 1 CHEVIRE-VERTOU | 17T000000020461H | RTE | CHEVIRE | VERTOU | 220 | 706 | 821 | 821 | 911 | [5 empty] | 1.074 | 4.891 | 33.098 | 11.895
LIT 225kV N0 1 CHOLET - MAUGES (LES) | 17T000000020541J | RTE | CHOLET | MAUGES (LES) | 220 | 1249 | 1337 | 1337 | 1434 | [5 empty] | 1.565 | 10.41 | 75.378 | 25.072
LIT 225kV N0 1 CHOLET-DISTRE | 17T000000020540L | RTE | CHOLET | DISTRE | 220 | 915 | 915 | 1075 | 1075 | [5 empty] | 3.953 | 26.547 | 201.08 | 66.007
LIT 225kV N0 1 CHOLET-VAL-DE-SEVRE | 17T0000000205639 | RTE | CHOLET | VAL-DE-SEVRE | 220 | 803 | 858 | 858 | 918 | [5 empty] | 4.502 | 16.299 | 106.314 | 38.688
LIT 225kV N0 1 CHOOZ-MAZURES | 17T0000000205744 | RTE | CHOOZ | MAZURES | 220 | 1100 | 1187 | 1187 | 1302 | [5 empty] | 0.852 | 8.755 | 115.274 | 29.393
LIT 225kV N0 1 CIROLLIERS - LOGES (LES) | 17T000000020611O | RTE | CIROLLIERS | LOGES (LES) | 220 | 880 | 880 | 1130 | 1130 | [5 empty] | 0.4 | 2.709 | 70.748 | 7.205
LIT 225kV N0 1 CISSAC-MARQUIS (LE) | 17T0000000206457 | RTE | CISSAC | MARQUIS (LE) | 220 | 1172 | 1248 | 1248 | 1310 | [5 empty] | 2.285 | 15.118 | 216.42 | 39.31
LIT 225kV N0 1 CIZE-FLEYRIAT | 17T000000020660B | RTE | CIZE | FLEYRIAT | 220 | 1059 | 1067 | 1141 | 1212 | [5 empty] | 1.216 | 7.669 | 114.862 | 24.233
LIT 225kV N0 1 CIZE-IZERNORE | 17T0000000206619 | RTE | CIZE | IZERNORE | 220 | 1059 | 1141 | 1141 | 1215 | [5 empty] | 0.454 | 2.701 | 20.04 | 6.97
LIT 225kV N0 1 CLEON-GRAND-COURONNE | 17T000000020722F | RTE | CLEON | GRAND-COURONNE | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 0.328 | 2.197 | 15.752 | 5.47
LIT 225kV N0 1 CLEON-MANOIR (LE) | 17T000000020723D | RTE | CLEON | MANOIR (LE) | 220 | 1270 | 1366 | 1366 | 1433 | [5 empty] | 0.88 | 5.92 | 42 | 14.651
LIT 225kV N0 1 COLAYRAC-DONZAC | 17T000000020811G | RTE | COLAYRAC | DONZAC | 220 | 831 | 984 | 984 | 1099 | [5 empty] | 1.756 | 11.772 | 83.6 | 29.278
LIT 225kV N0 1 COLAYRAC-GUPIE | 17T000000020812E | RTE | COLAYRAC | GUPIE | 220 | 895 | 980 | 980 | 1070 | [5 empty] | 3.214 | 21.383 | 154.774 | 53.496
LIT 225kV N0 1 COMMERVEIL-CHAMPFLEUR | 17T000000020891T | RTE | COMMERVEIL | CHAMPFLEUR | 220 | 1249 | 1316 | 1316 | 1389 | [5 empty] | 1.317 | 8.75 | 63.556 | 21.943
LIT 225kV N0 1 COMPIEGNE-LATENA | 17T0000000209324 | RTE | COMPIEGNE | LATENA | 220 | 881 | 964 | 964 | 1040 | [5 empty] | 3.041 | 14.566 | 98.936 | 35.41
LIT 225kV N0 1 COMPIEGNE-MORU | 17T0000000209332 | RTE | COMPIEGNE | MORU | 220 | 716 | 817 | 817 | 910 | [5 empty] | 1.82 | 8.91 | 58.9 | 21.472
LIT 225kV N0 1 CONCARNEAU - POTEAU-ROUGE | 17T0000000209413 | RTE | CONCARNEAU | POTEAU-ROUGE | 220 | 1056 | 1123 | 1123 | 1189 | [5 empty] | 3.245 | 22.203 | 163.358 | 56.304
LIT 225kV N0 1 CONCARNEAU-SQUIVIDAN | 17T000000020962W | RTE | CONCARNEAU | SQUIVIDAN | 220 | 1056 | 1123 | 1123 | 1189 | [5 empty] | 1.516 | 10.244 | 75.056 | 26.103
LIT 225kV N0 1 CONFLUENT-CHAMPAGNIER | 17T000000020970X | RTE | CONFLUENT | CHAMPAGNIER | 220 | 618 | 718 | 718 | 800 | [5 empty] | 1.76 | 9.15 | 60 | 22.412
LIT 225kV N0 1 CONFLUENT-PARISET | 17T000000020971V | RTE | CONFLUENT | PARISET | 220 | 850 | 850 | 1078 | 1078 | [5 empty] | 0.12 | 0.78 | 18 | 2.045
LIT 225kV N0 1 CONTAMINE-GRAND-COEUR | 17T000000021008W | RTE | CONTAMINE | GRAND-COEUR | 220 | 966 | 1076 | 1076 | 1168 | [5 empty] | 0.548 | 3.245 | 24.25 | 8.384
LIT 225kV N0 1 CONTAMINE-MALGOVERT | 17T000000021009U | RTE | CONTAMINE | MALGOVERT | 220 | 565 | 673 | 673 | 765 | [5 empty] | 2.26 | 10.86 | 76 | 27.527
LIT 225kV N0 1 COQUAINVILLIERS-DRONNIERE (LA) | 17T000000021043U | RTE | COQUAINVILLIERS | DRONNIERE (LA) | 220 | 955 | 955 | 1130 | 1130 | [5 empty] | 2.484 | 16.711 | 138.072 | 41.564
LIT 225kV N0 1 COQUAINVILLIERS-ROUGEMONTIER | 17T000000021044S | RTE | COQUAINVILLIERS | ROUGEMONTIER | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 2.797 | 18.835 | 133.302 | 46.232
LIT 225kV N0 1 COQUAINVILLIERS-TOURBE | 17T000000021045Q | RTE | COQUAINVILLIERS | TOURBE | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 2.212 | 14.928 | 105.01 | 36.875
LIT 225kV N0 1 CORBIERE (LA)-DISTRE | 17T0000000211015 | RTE | CORBIERE (LA) | DISTRE | 220 | 1213 | 1298 | 1298 | 1375 | [5 empty] | 2.766 | 18.428 | 127.554 | 45.457
LIT 225kV N0 1 CORDEMAIS-POSTE - PIQUAGE A BASTILLE |  | RTE | CORDEMAIS-POSTE | PIQUAGE A PLUVIGNER | 220 | 1175 | 1258 | 1258 | 1347 | [5 empty] | 1.079 | 7.31 | 54.226 | 19.931
LIT 225kV N0 1 CORDEMAIS-POSTE-PONTCHATEAU | 17T000000021050X | RTE | CORDEMAIS-POSTE | PONTCHATEAU | 220 | 829 | 909 | 909 | 984 | [5 empty] | 2.524 | 12.411 | 86.986 | 30.704
LIT 225kV N0 1 CORNIER-PRESSY | 17T000000021171L | RTE | CORNIER | PRESSY | 220 | 966 | 1076 | 1076 | 1168 | [5 empty] | 1.453 | 8.965 | 66.422 | 22.797
LIT 225kV N0 1 COSSIGNY-MORBRAS | 17T000000021225O | RTE | COSSIGNY | MORBRAS | 220 | 888 | 972 | 972 | 1049 | [5 empty] | 0.516 | 2.482 | 17.342 | 6.135
LIT 225kV N0 1 COUCHEY-CHAMPVANS | 17T000000021263G | RTE | COUCHEY | CHAMPVANS | 220 | 847 | 985 | 985 | 1116 | [5 empty] | 2.388 | 15.865 | 115.14 | 39.71
LIT 225kV N0 1 COUCHEY-VIELMOULIN | 17T000000021264E | RTE | COUCHEY | VIELMOULIN | 220 | 800 | 900 | 900 | 1000 | [5 empty] | 1.798 | 11.941 | 86.728 | 29.9
LIT 225kV N0 1 COUDON (LE) - NEOULES | 17T000000021273D | RTE | COUDON (LE) | NEOULES | 220 | 1001 | 1093 | 1093 | 1165 | [5 empty] | 1.094 | 6.574 | 48.078 | 16.595
LIT 225kV N0 1 COUDON (LE)-ESCAILLON (L ) | 17T000000021271H | RTE | COUDON (LE) | ESCAILLON (L ) | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 0.786 | 5.258 | 38.568 | 13.2
LIT 225kV N0 1 COURTRY-SENART | 17T000000021965L | RTE | COURTRY | SENART | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 1.073 | 7.207 | 96.418 | 18.326
LIT 225kV N0 1 CRECHETS (LES) - WEPPES | 17T000000021488T | RTE | CRECHETS (LES) | WEPPES | 220 | 1273 | 1346 | 1346 | 1453 | [5 empty] | 0.876 | 5.842 | 42.222 | 14.607
LIT 225kV N0 1 CRECHETS (LES)-GUARBECQUE | 17T000000021486X | RTE | CRECHETS (LES) | GUARBECQUE | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 1.43 | 9.5 | 69.034 | 23.478
LIT 225kV N0 1 CRENEY - FRONCLES | 17T000000021500S | RTE | CRENEY | FRONCLES | 220 | 899 | 984 | 984 | 1061 | [5 empty] | 6.818 | 34.112 | 240.424 | 84.751
LIT 225kV N0 1 CRENEY-ROSIERES | 17T000000021522I | RTE | CRENEY | ROSIERES | 220 | 899 | 984 | 984 | 1061 | [5 empty] | 2.31 | 12.393 | 84.042 | 30.108
LIT 225kV N0 1 CRETAINE-TOLBIAC | 17T000000021534B | RTE | CRETAINE | TOLBIAC | 220 | 620 | 620 | 690 | 690 | [5 empty] | 0.16 | 0.48 | 216 | 4.386
LIT 225kV N0 1 CROIX-DE-METZ-LANEUVEVILLE | 17T0000000192786 | RTE | CROIX-DE-METZ | LANEUVEVILLE | 220 | 899 | 984 | 984 | 1061 | [5 empty] | 2.836 | 15.641 | 111.8 | 39.04
LIT 225kV N0 1 CROIX-DE-METZ-VOID | 17T0000000192794 | RTE | CROIX-DE-METZ | VOID | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 1.931 | 12.851 | 93.11 | 32.175
LIT 225kV N0 1 CUBNEZAIS-GREZILLAC | 17T0000000217408 | RTE | CUBNEZAIS | GREZILLAC | 220 | 932 | 1049 | 1049 | 1126 | [5 empty] | 1.983 | 13.287 | 98.738 | 34.16
LIT 225kV N0 1 CUBNEZAIS-MARQUIS (LE) | 17T0000000217416 | RTE | CUBNEZAIS | MARQUIS (LE) | 220 | 1748 | 2048 | 2048 | 2222 | [5 empty] | 0.359 | 3.488 | 44.08 | 11.884
LIT 225kV N0 1 CUBNEZAIS-MONTGUYON | 17T000000021762Z | RTE | CUBNEZAIS | MONTGUYON | 220 | 951 | 1104 | 1104 | 1170 | [5 empty] | 2.529 | 14.39 | 108.16 | 36.716
LIT 225kV N0 1 CUBNEZAIS-TUILIERES | 17T000000021763X | RTE | CUBNEZAIS | TUILIERES | 220 | 1080 | 1185 | 1185 | 1289 | [5 empty] | 3.867 | 26.093 | 452.464 | 95.931
LIT 225kV N0 1 DAMERY-NOGENTEL | 17T000000022051Q | RTE | DAMERY | NOGENTEL | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 2.257 | 15.015 | 108.748 | 37.72
LIT 225kV N0 1 DAMERY-VESLE | 17T000000022052O | RTE | DAMERY | VESLE | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 2.612 | 17.457 | 125.708 | 43.188
LIT 225kV N0 1 DANTOU-TUILIERES | 17T0000000220891 | RTE | DANTOU | TUILIERES | 220 | 642 | 757 | 757 | 845 | [5 empty] | 4.112 | 18.659 | 129.344 | 45.976
LIT 225kV N0 1 DANTOU-VERLHAGUET | 17T000000022090G | RTE | DANTOU | VERLHAGUET | 220 | 289 | 543 | 543 | 682 | [5 empty] | 5.605 | 25.282 | 175.102 | 66.225
LIT 225kV N0 1 DARSE - FEUILLANE | 17T000000022130U | RTE | DARSE | FEUILLANE | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 0.787 | 5.273 | 37.766 | 13.143
LIT 225kV N0 1 DARSE-RASSUEN | 17T000000022132Q | RTE | DARSE | RASSUEN | 220 | 795 | 795 | 970 | 970 | [5 empty] | 1.028 | 6.364 | 216.614 | 17.682
LIT 225kV N0 1 DECHY - GAVRELLE | 17T000000022171G | RTE | DECHY | GAVRELLE | 220 | 975 | 1030 | 1030 | 1110 | [5 empty] | 2.42 | 12.124 | 98.674 | 30.663
LIT 225kV N0 1 DECHY-MASTAING | 17T000000022172E | RTE | DECHY | MASTAING | 220 | 935 | 1000 | 1000 | 1080 | [5 empty] | 1.705 | 18.414 | 54.262 | 19.226
LIT 225kV N0 1 DIGUE-DES-FRANCAIS-LINGOSTIERE | 17T000000021978C | RTE | DIGUE-DES-FRANCAIS | LINGOSTIERE | 220 | 708 | 708 | 847 | 847 | [5 empty] | 0.308 | 2.045 | 186.588 | 6.54
LIT 225kV N0 1 DISTRE - MONDION | 17T0000000222835 | RTE | DISTRE | MONDION | 220 | 957 | 1023 | 1023 | 1096 | [5 empty] | 4.824 | 21.992 | 152.554 | 53.588
LIT 225kV N0 1 DOBERIE - RANCE-POSTE | 17T000000022299R | RTE | DOBERIE | RANCE-POSTE | 220 | 1104 | 1222 | 1222 | 1315 | [5 empty] | 2.133 | 14.721 | 108.514 | 37.272
LIT 225kV N0 1 DOBERIE - TREGUEUX | 17T000000022300V | RTE | DOBERIE | TREGUEUX | 220 | 1217 | 1266 | 1266 | 1322 | [5 empty] | 1.421 | 9.807 | 72.364 | 24.854
LIT 225kV N0 1 DONZAC-VERLHAGUET | 17T000000022378V | RTE | DONZAC | VERLHAGUET | 220 | 831 | 960 | 984 | 1099 | [5 empty] | 2.644 | 17.552 | 150.1 | 44.328
LIT 225kV N0 1 DONZENAC-FEROUGE | 17T000000022407D | RTE | DONZENAC | FEROUGE | 220 | 814 | 983 | 983 | 1099 | [5 empty] | 2.58 | 17.133 | 124.558 | 43.009
LIT 225kV N0 1 DRONNIERE (LA) - TOURBE | 17T000000022487Q | RTE | DRONNIERE (LA) | TOURBE | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 0.614 | 4.094 | 29.594 | 10.567
LIT 225kV N0 1 DRONNIERE (LA)-FLERS | 17T000000022485U | RTE | DRONNIERE (LA) | FLERS | 220 | 1250 | 1312 | 1312 | 1375 | [5 empty] | 2.977 | 20.563 | 151.634 | 52.33
LIT 225kV N0 1 DUVIGNEAU - PIQUAGE A DUVIGNEAU |  | RTE | DUVIGNEAU | PIQUAGE A DUVIGNEAU | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 0.018 | 0.116 | 0.846 | 0.292
LIT 225kV N0 1 ECHALAS - GIVORS | 17T000000022602F | RTE | ECHALAS | GIVORS | 220 | 900 | 910 | 1015 | 1080 | [5 empty] | 0.42 | 2.89 | 36 | 6.946
LIT 225kV N0 1 ECHALAS-RIVIERE (LA) | 17T000000022604B | RTE | ECHALAS | RIVIERE (LA) | 220 | 1800 | 2030 | 2030 | 2224 | [5 empty] | 0.865 | 8.422 | 114.164 | 28.844
LIT 225kV N0 1 ECHALAS-SOLEIL (LE) | 17T0000000226059 | RTE | ECHALAS | SOLEIL (LE) | 220 | 1375 | 1437 | 1437 | 1500 | [5 empty] | 0.89 | 8.83 | 108 | 28.207
LIT 225kV N0 1 ECHINGHEN-MANDARINS | 17T000000022621B | RTE | ECHINGHEN | MANDARINS | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 1.919 | 12.79 | 92.422 | 31.993
LIT 225kV N0 1 ECHINGHEN-SORRUS | 17T0000000226423 | RTE | ECHINGHEN | SORRUS | 220 | 935 | 935 | 935 | 935 | [5 empty] | 2.65 | 12.047 | 83.552 | 29.715
LIT 225kV N0 1 EGUZON-MARMAGNE | 17T000000022684O | RTE | EGUZON | MARMAGNE | 220 | 274 | 412 | 412 | 476 | [5 empty] | 14.456 | 40.726 | 260.12 | 92.576
LIT 225kV N0 1 EGUZON-MAUREIX (LE) | 17T000000022685M | RTE | EGUZON | MAUREIX (LE) | 220 | 905 | 1003 | 1003 | 1063 | [5 empty] | 6.387 | 30.781 | 216.41 | 76.254
LIT 225kV N0 1 EGUZON-MONTLUCON | 17T000000022687I | RTE | EGUZON | MONTLUCON | 220 | 497 | 596 | 596 | 663 | [5 empty] | 10.43 | 34.48 | 214 | 79.482
LIT 225kV N0 1 EGUZON-MOUSSEAUX | 17T000000022686K | RTE | EGUZON | MOUSSEAUX | 220 | 520 | 831 | 831 | 895 | [5 empty] | 4.591 | 21.708 | 170.066 | 51.013
LIT 225kV N0 1 EGUZON-ORANGERIE (L) | 17T000000022688G | RTE | EGUZON | ORANGERIE (L) | 220 | 409 | 644 | 644 | 761 | [5 empty] | 8.454 | 38.123 | 264.178 | 94.599
LIT 225kV N0 1 EGUZON-STE-FEYRE | 17T000000022689E | RTE | EGUZON | STE-FEYRE | 220 | 832 | 921 | 921 | 975 | [5 empty] | 3.918 | 16.521 | 120.262 | 41.628
LIT 225kV N0 1 ELANCOURT-MEZEROLLES | 17T000000022728U | RTE | ELANCOURT | MEZEROLLES | 220 | 1140 | 1248 | 1248 | 1347 | [5 empty] | 1.676 | 10.871 | 79.966 | 27.54
LIT 225kV N0 1 ELANCOURT-ST-AUBIN | 17T0000000227306 | RTE | ELANCOURT | ST-AUBIN | 220 | 511 | 768 | 768 | 979 | [5 empty] | 1.122 | 7.373 | 58.858 | 18.556
LIT 225kV N0 1 ELANCOURT-YVELINES-OUEST | 17T0000000227322 | RTE | ELANCOURT | YVELINES-OUEST | 220 | 1056 | 1056 | 1360 | 1360 | [5 empty] | 0.298 | 2.013 | 939.37 | 12.751
LIT 225kV N0 1 ENCO-DE-BOTTE - RABATAU | 17T0000000225338 | RTE | ENCO-DE-BOTTE | RABATAU | 220 | 400 | 400 | 715 | 715 | [5 empty] | 0.713 | 4.3 | 463.67 | 14.103
LIT 225kV N0 1 ENCO-DE-BOTTE - REALTOR | 17T0000000225346 | RTE | ENCO-DE-BOTTE | REALTOR | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 1.336 | 8.918 | 64.174 | 23.562
LIT 225kV N0 1 ENCO-DE-BOTTE-PALUN (LA) | 17T000000022532A | RTE | ENCO-DE-BOTTE | PALUN (LA) | 220 | 1001 | 1093 | 1093 | 1165 | [5 empty] | 1.12 | 7.113 | 50.894 | 17.835
LIT 225kV N0 1 ENVAL-ISSOIRE | 17T000000022775L | RTE | ENVAL | ISSOIRE | 220 | 617 | 740 | 740 | 826 | [5 empty] | 2.87 | 13.21 | 94 | 31.568
LIT 225kV N0 1 ENVAL-VOLVIC | 17T000000022776J | RTE | ENVAL | VOLVIC | 220 | 814 | 983 | 983 | 1099 | [5 empty] | 0.87 | 6.07 | 42 | 15.031
LIT 225kV N0 1 ESCAILLON (L ) - NEOULES | 17T000000022852T | RTE | ESCAILLON (L ) | NEOULES | 220 | 935 | 935 | 1085 | 1085 | [5 empty] | 0.956 | 7.044 | 795.338 | 24.415
LIT 225kV N0 1 FALLOU-NOVION | 17T000000023144E | RTE | FALLOU | NOVION | 220 | 620 | 620 | 690 | 690 | [5 empty] | 0.157 | 0.536 | 466.496 | 49.98
LIT 225kV N0 1 FAMARS-GROS-CAILLOU | 17T0000000231583 | RTE | FAMARS | GROS-CAILLOU | 220 | 975 | 1030 | 1030 | 1110 | [5 empty] | 1.407 | 6.986 | 49.168 | 17.235
LIT 225kV N0 1 FARRADIERE (LA) - SAINTES | 17T000000023188V | RTE | FARRADIERE (LA) | SAINTES | 220 | 1180 | 1310 | 1310 | 1390 | [5 empty] | 1.912 | 12.791 | 120.482 | 32.262
LIT 225kV N0 1 FARRADIERE (LA)-GRANZAY | 17T000000023187X | RTE | FARRADIERE (LA) | GRANZAY | 220 | 1249 | 1337 | 1337 | 1434 | [5 empty] | 2.551 | 17.077 | 122.274 | 43.118
LIT 225kV N0 1 FEROUGE-TALAMET | 17T000000023224G | RTE | FEROUGE | TALAMET | 220 | 895 | 980 | 980 | 1070 | [5 empty] | 2.487 | 16.515 | 120.06 | 41.489
LIT 225kV N0 1 FEUILLANE - PONTEAU | 17T0000000232628 | RTE | FEUILLANE | PONTEAU | 220 | 1375 | 1437 | 1437 | 1500 | [5 empty] | 0.554 | 5.84 | 71.264 | 19.037
LIT 225kV N0 1 FEUILLANE-LAVERA | 17T000000023241G | RTE | FEUILLANE | LAVERA | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 1.021 | 6.858 | 48.694 | 17.02
LIT 225kV N0 1 FEUILLANE-ST-CHAMAS | 17T0000000232652 | RTE | FEUILLANE | ST-CHAMAS | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 2.041 | 13.924 | 101.92 | 35.58
LIT 225kV N0 1 FLANDRE - ROMAINVILLE | 17T000000023241G | RTE | FLANDRE | ROMAINVILLE | 220 | 633 | 633 | 738 | 738 | [5 empty] | 0.16 | 0.64 | 280 | 5.295
LIT 225kV N0 1 FLEAC-MARQUIS (LE) | 17T000000023359U | RTE | FLEAC | MARQUIS (LE) | 220 | 1112 | 1233 | 1233 | 1307 | [5 empty] | 5.538 | 36.782 | 266.444 | 92.259
LIT 225kV N0 1 FLEAC-MONTGUYON | 17T0000000233608 | RTE | FLEAC | MONTGUYON | 220 | 831 | 921 | 921 | 975 | [5 empty] | 7.482 | 26.459 | 164.464 | 62.46
LIT 225kV N0 1 FLEAC-NIORT | 17T0000000233616 | RTE | FLEAC | NIORT | 220 | 524 | 644 | 644 | 717 | [5 empty] | 10.395 | 37.201 | 231.83 | 86.837
LIT 225kV N0 1 FLEAC-SANILHAC | 17T000000023382Z | RTE | FLEAC | SANILHAC | 220 | 642 | 757 | 757 | 845 | [5 empty] | 8.058 | 36.644 | 252.518 | 90.158
LIT 225kV N0 1 FLERS-LAUNAY | 17T000000023388N | RTE | FLERS | LAUNAY | 220 | 539 | 675 | 675 | 781 | [5 empty] | 5.018 | 22.63 | 359.494 | 57.88
LIT 225kV N0 1 FLEYRIAT-VOUGLANS | 17T000000023400M | RTE | FLEYRIAT | VOUGLANS | 220 | 850 | 959 | 959 | 1050 | [5 empty] | 2.82 | 17.02 | 124 | 42.068
LIT 225kV N0 1 FLOIRAC-MARQUIS (LE) | 17T0000000234345 | RTE | FLOIRAC | MARQUIS (LE) | 220 | 929 | 965 | 1088 | 1140 | [5 empty] | 1.506 | 9.859 | 99.562 | 24.72
LIT 225kV N0 1 FLOIRAC-PESSAC | 17T0000000234353 | RTE | FLOIRAC | PESSAC | 220 | 932 | 1049 | 1049 | 1126 | [5 empty] | 1.347 | 9.018 | 64.71 | 22.465
LIT 225kV N0 1 FLORENSAC - ST VINCENT | 17T000000023440A | RTE | FLORENSAC | ST-VINCENT | 220 | 1161 | 1241 | 1241 | 1306 | [5 empty] | 1.705 | 10.144 | 75.326 | 25.831
LIT 225kV N0 1 FONT (LA)-RIORGES | 17T000000023475S | RTE | FONT (LA) | RIORGES | 220 | 358 | 692 | 692 | 883 | [5 empty] | 3.015 | 20.203 | 146.744 | 50.746
LIT 225kV N0 1 FOUSCAIS - TAMAREAU | 17T000000023529V | RTE | FOUSCAIS | TAMAREAU | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 1.495 | 10.017 | 71.742 | 24.931
LIT 225kV N0 1 FREJUS-TRANS | 17T000000023588F | RTE | FREJUS | TRANS | 220 | 1062 | 1066 | 1160 | 1238 | [5 empty] | 1.383 | 9.223 | 94.796 | 22.8
LIT 225kV N0 1 GAMPALOUP - PONT-EVEQUE | 17T000000023882F | RTE | GAMPALOUP | PONT-EVEQUE | 220 | 880 | 992 | 992 | 1086 | [5 empty] | 1.43 | 9.66 | 68 | 24.656
LIT 225kV N0 1 GANGES - ST VICTOR | 17T0000000238867 | RTE | GANGES | ST-VICTOR | 220 | 325 | 457 | 457 | 572 | [5 empty] | 10.901 | 30.969 | 220.554 | 77.078
LIT 225kV N0 1 GANGES - VIRADEL | 17T0000000238875 | RTE | GANGES | VIRADEL | 220 | 302 | 424 | 424 | 531 | [5 empty] | 6.56 | 23.93 | 158.908 | 58.068
LIT 225kV N0 1 GARCHIZY-ST-ELOI | 17T000000023899Z | RTE | GARCHIZY | ST-ELOI | 220 | 814 | 930 | 983 | 1099 | [5 empty] | 0.689 | 4.611 | 59.49 | 12.095
LIT 225kV N0 1 GAVRELLE - TRAN5 / GAVRE PERTA 1 | 17T0000000240396 | RTE | GAVRELLE | TRAN5 / GAVRE PERTA 1 | 220 | 956 | 1110 | 1110 | 1088 | [5 empty] | 3.154 | 14.315 | 96.496 | 34.72
LIT 225kV N0 1 GENISSIAT-POSTE-IZERNORE | 17T0000000240671 | RTE | GENISSIAT-POSTE | IZERNORE | 220 | 862 | 928 | 928 | 987 | [5 empty] | 1.928 | 9.402 | 109.27 | 27.258
LIT 225kV N0 1 GENISSIAT-POSTE-SERRIERES | 17T000000024069Y | RTE | GENISSIAT-POSTE | SERRIERES | 220 | 477 | 566 | 566 | 642 | [5 empty] | 1.98 | 8.5 | 56 | 20.269
LIT 225kV N0 1 GENISSIAT-POSTE-VOUGLANS | 17T000000024070C | RTE | GENISSIAT-POSTE | VOUGLANS | 220 | 853 | 991 | 991 | 1118 | [5 empty] | 2.558 | 15.756 | 116.282 | 40.005
LIT 225kV N0 1 GINESTOUS-LESQUIVE | 17T000000024187S | RTE | GINESTOUS | LESQUIVE | 220 | 1080 | 1185 | 1185 | 1289 | [5 empty] | 1.645 | 10.967 | 79.198 | 27.394
LIT 225kV N0 1 GIVORS - MIONS | 17T000000024195T | RTE | GIVORS | MIONS | 220 | 695 | 782 | 782 | 940 | [5 empty] | 1.62 | 8.05 | 70 | 19.391
LIT 225kV N0 1 GIVORS-BANS-GIVORS | 17T000000023676I | RTE | GIVORS-BANS | GIVORS | 220 | 900 | 1015 | 1015 | 1112 | [5 empty] | 0.02 | 0.19 | 0 | 0.558
LIT 225kV N0 1 GODIN-RUEYRES | 17T000000024230G | RTE | GODIN | RUEYRES | 220 | 637 | 706 | 706 | 793 | [5 empty] | 4.693 | 19.594 | 125.698 | 46.373
LIT 225kV N0 1 GODIN-ST-VICTOR | 17T000000024231E | RTE | GODIN | ST-VICTOR | 220 | 442 | 511 | 511 | 577 | [5 empty] | 11.175 | 31.341 | 199.702 | 74.374
LIT 225kV N0 1 GODIN-VERLHAGUET | 17T000000024232C | RTE | GODIN | VERLHAGUET | 220 | 819 | 897 | 897 | 974 | [5 empty] | 8.815 | 41.177 | 261.48 | 96.865
LIT 225kV N0 1 GOURJADE - VERFEIL | 17T0000000243425 | RTE | GOURJADE | VERFEIL | 220 | 828 | 908 | 908 | 986 | [5 empty] | 5.828 | 28.348 | 198.254 | 69.653
LIT 225kV N0 1 GRAFFENSTADEN-MARLENHEIM | 17T0000000243603 | RTE | GRAFFENSTADEN | MARLENHEIM | 220 | 843 | 909 | 909 | 996 | [5 empty] | 1.507 | 7.466 | 51.896 | 18.385
LIT 225kV N0 1 GRAFFENSTADEN-SCHEER | 17T000000024363Y | RTE | GRAFFENSTADEN | SCHEER | 220 | 654 | 758 | 758 | 857 | [5 empty] | 2.123 | 9.657 | 66.184 | 23.641
LIT 225kV N0 1 GRAND-COURONNE-ROUGEMONTIER | 17T000000023724X | RTE | GRAND-COURONNE | ROUGEMONTIER | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 1.423 | 9.529 | 68.33 | 23.798
LIT 225kV N0 1 GRAND-COURONNE-ST ETIENNE DU ROUVRAY | 17T000000023725V | RTE | GRAND-COURONNE | ST ETIENNE DU ROUVRAY | 220 | 1300 | 1350 | 1350 | 1400 | [5 empty] | 0.544 | 3.646 | 26.124 | 9.071
LIT 225kV N0 1 GRAND-COURONNE-VAUPALIERE (LA) | 17T000000023726T | RTE | GRAND-COURONNE | VAUPALIERE (LA) | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 1.559 | 10.443 | 74.378 | 25.989
LIT 225kV N0 1 GRANDE-SYNTHE-HOLQUE | 17T000000023809P | RTE | GRANDE-SYNTHE | HOLQUE | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 1.146 | 7.622 | 55.274 | 19.435
LIT 225kV N0 1 GRANDE-SYNTHE-WARANDE | 17T000000023813Y | RTE | GRANDE-SYNTHE | WARANDE | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 0.884 | 5.897 | 42.576 | 14.722
LIT 225kV N0 1 GRAND-QUEVILLY-VAUPALIERE (LA) | 17T000000023776E | RTE | GRAND-QUEVILLY | VAUPALIERE (LA) | 220 | 820 | 820 | 1040 | 1040 | [5 empty] | 0.56 | 3.82 | 70 | 9.478
LIT 225kV N0 1 GRANDVAL-PRATCLAUX | 17T000000024371Z | RTE | GRANDVAL | PRATCLAUX | 220 | 790 | 790 | 862 | 926 | [5 empty] | 4.456 | 19.925 | 135.266 | 49.036
LIT 225kV N0 1 GRANZAY-NIORT | 17T000000024375R | RTE | GRANZAY | NIORT | 220 | 1249 | 1337 | 1337 | 1434 | [5 empty] | 1.599 | 10.685 | 76.534 | 26.683
LIT 225kV N0 1 GRANZAY-ST-FLORENT | 17T000000024376P | RTE | GRANZAY | ST-FLORENT | 220 | 1249 | 1337 | 1337 | 1434 | [5 empty] | 0.644 | 4.29 | 31.018 | 10.767
LIT 225kV N0 1 GREZILLAC - PIQUAGE A FONCROSE |  | RTE | GREZILLAC | PIQUAGE A FONCROSE | 220 | 932 | 1049 | 1049 | 1126 | [5 empty] | 0.955 | 6.332 | 46.082 | 16
LIT 225KV N0 1 GRIMAUD - TRANS | 17T000000024459L | RTE | GRIMAUD | TRANS | 220 | 686 | 686 | 686 | 816 | [5 empty] | 1.682 | 11.13 | 309.878 | 29.772
LIT 225kV N0 1 GRISOLLES-SERRE-PONCON | 17T000000024490R | RTE | GRISOLLES | SERRE-PONCON | 220 | 1059 | 1141 | 1141 | 1215 | [5 empty] | 1.064 | 6.729 | 48.926 | 17.195
LIT 225kV N0 1 GROS-CAILLOU-MASTAING | 17T000000023681P | RTE | GROS-CAILLOU | MASTAING | 220 | 1273 | 1346 | 1346 | 1453 | [5 empty] | 0.253 | 1.676 | 12.2 | 4.208
LIT 225kV N0 1 GROSNE-GUEUGNON | 17T000000024491P | RTE | GROSNE | GUEUGNON | 220 | 814 | 983 | 983 | 1099 | [5 empty] | 3.29 | 21.899 | 158.622 | 54.965
LIT 225kV N0 1 GROSNE-MACON | 17T000000024492N | RTE | GROSNE | MACON | 220 | 618 | 718 | 718 | 807 | [5 empty] | 1.892 | 19.148 | 215.058 | 59.04
LIT 225kV N0 1 GUEBWILLER - LOGELBACH | 17T000000024529Q | RTE | GUEBWILLER | LOGELBACH | 220 | 1070 | 1155 | 1155 | 1265 | [5 empty] | 1.722 | 11.524 | 81.652 | 28.559
LIT 225kV N0 1 GUEBWILLER - VOGELGRUN | 17T0000000245304 | RTE | GUEBWILLER | VOGELGRUN | 220 | 1070 | 1155 | 1155 | 1265 | [5 empty] | 2.087 | 13.943 | 98.342 | 34.526
LIT 225kV N0 1 GUEUGNON - HENRI-PAUL | 17T000000024579B | RTE | GUEUGNON | HENRI-PAUL | 220 | 715 | 897 | 897 | 1032 | [5 empty] | 2.391 | 15.925 | 170.214 | 40.553
LIT 225kV N0 1 GUPIE - PIQUAGE A FONCROSE |  | RTE | GUPIE | PIQUAGE A FONCROSE | 220 | 831 | 984 | 984 | 1099 | [5 empty] | 1.68 | 11.144 | 81.104 | 28
LIT 225kV N0 1 HAVRE (LE) (POSTE) - PONT-SEPT | 17T000000024774D | RTE | HAVRE (LE) (POSTE) | PONT-SEPT | 220 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.119 | 1.154 | 15.594 | 3.952
LIT 225kV N0 1 HOLQUE-LONGUENESSE | 17T0000000248749 | RTE | HOLQUE | LONGUENESSE | 220 | 969 | 969 | 1061 | 1061 | [5 empty] | 0.782 | 5.214 | 46.882 | 12.938
LIT 225kV N0 1 HOLQUE-WARANDE | 17T0000000248765 | RTE | HOLQUE | WARANDE | 220 | 1300 | 1350 | 1350 | 1400 | [5 empty] | 1.263 | 8.407 | 60.81 | 21.021
LIT 225kV N0 1 HOURAT (LE)-MARSILLON | 17T000000024900Y | RTE | HOURAT (LE) | MARSILLON | 220 | 419 | 580 | 580 | 720 | [5 empty] | 4.321 | 19.708 | 133.934 | 48.124
LIT 225kV N0 1 HOURAT (LE)-MIEGEBAT | 17T000000024901W | RTE | HOURAT (LE) | MIEGEBAT | 220 | 392 | 542 | 542 | 673 | [5 empty] | 0.556 | 2.595 | 16.956 | 6.195
LIT 225kV N0 1 ILE-NAPOLEON - OTTMARSHEIM | 17T000000024941K | RTE | ILE-NAPOLEON | OTTMARSHEIM | 220 | 1100 | 1187 | 1187 | 1302 | [5 empty] | 0.673 | 4.467 | 32.51 | 11.225
LIT 225kV N0 1 ILE-NAPOLEON-LUTTERBACH | 17T000000024940M | RTE | ILE-NAPOLEON | LUTTERBACH | 220 | 847 | 985 | 985 | 1116 | [5 empty] | 1.107 | 7.448 | 52.598 | 18.46
LIT 225kV N0 1 ISSOIRE-LIGNAT | 17T000000025014H | RTE | ISSOIRE | LIGNAT | 220 | 1002 | 1113 | 1113 | 1205 | [5 empty] | 1.28 | 8.47 | 60 | 20.903
LIT 225kV N0 1 ISSOIRE-PRATCLAUX | 17T000000025015F | RTE | ISSOIRE | PRATCLAUX | 220 | 770 | 928 | 928 | 1037 | [5 empty] | 4.546 | 30.66 | 206.564 | 74.277
LIT 225kV N0 1 JACQUARD-SOLEIL (LE) | 17T0000000250529 | RTE | JACQUARD | SOLEIL (LE) | 220 | 1123 | 1211 | 1211 | 1290 | [5 empty] | 1.008 | 6.752 | 48.4 | 16.737
LIT 225kV N0 1 JALIS-LESQUIVE | 17T000000025058Y | RTE | JALIS | LESQUIVE | 220 | 828 | 908 | 908 | 986 | [5 empty] | 5.569 | 28.651 | 202.786 | 71.153
LIT 225kV N0 1 JONQUIERES-ST-CESAIRE | 17T000000025122E | RTE | JONQUIERES | ST-CESAIRE | 220 | 1055 | 1055 | 1230 | 1230 | [5 empty] | 1.244 | 8.273 | 70.22 | 21.709
LIT 225kV N0 1 KEMBS-OTTMARSHEIM | 17T000000025205A | RTE | KEMBS | OTTMARSHEIM | 220 | 539 | 661 | 661 | 754 | [5 empty] | 1.24 | 5.637 | 39.536 | 13.944
LIT 225kV N0 1 KEMBS-SIERENTZ | 17T0000000252068 | RTE | KEMBS | SIERENTZ | 220 | 827 | 891 | 891 | 976 | [5 empty] | 0.335 | 1.586 | 10.494 | 3.807
LIT 225kV N0 1 LA GAUDIERE - LIVIERE | 17T000000023972E | RTE | GAUDIERE (LA) | LIVIERE | 220 | 1090 | 1090 | 1260 | 1260 | [5 empty] | 0.821 | 5.543 | 161.088 | 26.831
LIT 225kV N0 1 LA GAUDIERE - MOREAU | 17T000000023973C | RTE | GAUDIERE (LA) | MOREAU | 220 | 946 | 1010 | 1010 | 1063 | [5 empty] | 2.208 | 9.825 | 68.442 | 24.262
LIT 225kV N0 1 LA GAUDIERE - ST VINCENT | 17T000000023974A | RTE | GAUDIERE (LA) | ST-VINCENT | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 3.26 | 22.082 | 159.556 | 55.078
LIT 225kV N0 1 LANDERNEAU-LOSCOAT | 17T000000025419S | RTE | LANDERNEAU | LOSCOAT | 220 | 1212 | 1262 | 1262 | 1318 | [5 empty] | 1.551 | 10.314 | 74.634 | 25.862
LIT 225kV N0 1 LANDERNEAU-MARTYRE (LA) | 17T0000000254206 | RTE | LANDERNEAU | MARTYRE (LA) | 220 | 1217 | 1266 | 1266 | 1322 | [5 empty] | 0.222 | 1.324 | 9.78 | 3.87
LIT 225kV N0 1 LANDRES-MONTOIS | 17T000000025449J | RTE | LANDRES | MONTOIS | 220 | 1100 | 1187 | 1187 | 1302 | [5 empty] | 1.396 | 9.385 | 67.702 | 23.325
LIT 225kV N0 1 LANDRES-MOULAINE | 17T000000025448L | RTE | LANDRES | MOULAINE | 220 | 1070 | 1155 | 1155 | 1265 | [5 empty] | 1.207 | 8.015 | 55.542 | 19.7
LIT 225kV N0 1 LANDRES-STENAY | 17T000000025450Y | RTE | LANDRES | STENAY | 220 | 1100 | 1187 | 1187 | 1302 | [5 empty] | 2.804 | 19.287 | 142.414 | 49.025
LIT 225kV N0 1 LANDRES-VIGY | 17T000000025451W | RTE | LANDRES | VIGY | 220 | 1070 | 1155 | 1155 | 1265 | [5 empty] | 2.59 | 17.345 | 124.288 | 43.185
LIT 225kV N0 1 LANNEMEZAN-PRAGNERES | 17T-FR-000000600 | RTE | LANNEMEZAN | PRAGNERES | 220 | 737 | 820 | 820 | 889 | [5 empty] | 5.673 | 25.457 | 177.508 | 62.874
LIT 225kV N0 1 LATENA-PERTAIN | 17T0000000255877 | RTE | LATENA | PERTAIN | 220 | 1172 | 1235 | 1285 | 1388 | [5 empty] | 1.003 | 6.694 | 61.582 | 16.987
LIT 225kV N0 1 LATENA-ROYE | 17T0000000255885 | RTE | LATENA | ROYE | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 0.65 | 4.449 | 32.666 | 11.268
LIT 225kV N0 1 LAUNAY-RANCE-POSTE | 17T000000025592E | RTE | LAUNAY | RANCE-POSTE | 220 | 901 | 988 | 988 | 1050 | [5 empty] | 5.956 | 27.074 | 187.838 | 66.725
LIT 225kV N0 1 LAVERA - PONTEAU | 17T000000025662J | RTE | LAVERA | PONTEAU | 220 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.063 | 0.696 | 10.656 | 2.54
LIT 225kV N0 1 LAVERA - SEPTEMES | 17T000000025664F | RTE | LAVERA | SEPTEMES | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 1.732 | 11.488 | 83.594 | 28.904
LIT 225kV N0 1 LAVERA-PORT-DE-BOUC (CLIENT) | 17T000000025641R | RTE | LAVERA | PORT-DE-BOUC (CLIENT) | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 0.526 | 3.524 | 25.414 | 8.816
LIT 225kV N0 1 LAVEYRUNE - PRATCLAUX | 17T0000000256695 | RTE | LAVEYRUNE | PRATCLAUX | 220 | 315 | 443 | 443 | 546 | [5 empty] | 6.679 | 19.423 | 121.172 | 45.19
LIT 225kV N0 1 LEGUEVIN - PORTET-ST-SIMON | 17T000000025702X | RTE | LEGUEVIN | PORTET-ST-SIMON | 220 | 813 | 890 | 890 | 966 | [5 empty] | 1.616 | 7.481 | 49.398 | 17.986
LIT 225kV N0 1 LEGUEVIN-LESQUIVE | 17T000000025681F | RTE | LEGUEVIN | LESQUIVE | 220 | 813 | 890 | 890 | 966 | [5 empty] | 2.266 | 10.729 | 71.196 | 24.939
LIT 225KV N0 1 LESCAR - MARSILLON | 17T000000025715O | RTE | LESCAR | MARSILLON | 220 | 1172 | 1248 | 1248 | 1310 | [5 empty] | 1.083 | 7.281 | 77.858 | 18.3
LIT 225kV N0 1 LESQUIVE-VERLHAGUET | 17T0000000257497 | RTE | LESQUIVE | VERLHAGUET | 220 | 828 | 908 | 908 | 986 | [5 empty] | 2.045 | 9.143 | 68.406 | 24.271
LIT 225kV N0 1 LIGNAT-RULHAT | 17T000000025796Z | RTE | LIGNAT | RULHAT | 220 | 1032 | 1146 | 1146 | 1241 | [5 empty] | 0.633 | 4.196 | 28.704 | 10.255
LIT 225kV N0 1 LINGOSTIERE-TRINITE-VICTOR | 17T0000000258299 | RTE | LINGOSTIERE | TRINITE-VICTOR | 220 | 816 | 889 | 889 | 947 | [5 empty] | 1.092 | 4.937 | 34.558 | 12.188
LIT 225kV N0 1 LIVIERE - ST VINCENT | 17T0000000258671 | RTE | LIVIERE | ST-VINCENT | 220 | 1234 | 1320 | 1320 | 1389 | [5 empty] | 1.661 | 11.463 | 82.682 | 28.524
LIT 225kV N0 1 LONG-CHAMP (LE) - SOISSONS-NOTRE-DAME | 17T0000000252602 | RTE | LONG-CHAMP (LE) | SOISSONS-NOTRE-DAME | 220 | 731 | 835 | 835 | 925 | [5 empty] | 1.112 | 5.351 | 37.002 | 13.165
LIT 225kV N0 1 LOSCOAT-MARTYRE (LA) | 17T0000000259619 | RTE | LOSCOAT | MARTYRE (LA) | 220 | 1280 | 1332 | 1332 | 1382 | [5 empty] | 1.705 | 11.348 | 82.118 | 29.488
LIT 225kV N0 1 LUMES-MAZURES | 17T000000026039X | RTE | LUMES | MAZURES | 220 | 843 | 909 | 909 | 996 | [5 empty] | 1.937 | 9.449 | 66.334 | 23.715
LIT 225kV N0 1 LUMES-MOHON | 17T000000026040B | RTE | LUMES | MOHON | 220 | 647 | 749 | 749 | 847 | [5 empty] | 0.395 | 1.79 | 12.096 | 4.7
LIT 225kV N0 1 LUMES-STENAY | 17T0000000260419 | RTE | LUMES | STENAY | 220 | 1100 | 1187 | 1187 | 1302 | [5 empty] | 2.551 | 17.609 | 128.158 | 44.9
LIT 225kV N0 1 LUTTERBACH-SIERENTZ | 17T000000026057V | RTE | LUTTERBACH | SIERENTZ | 220 | 847 | 985 | 985 | 1116 | [5 empty] | 1.375 | 9.214 | 66.026 | 22.9
LIT 225kV N0 1 MALGOVERT-PASSY | 17T000000026274N | RTE | MALGOVERT | PASSY | 220 | 533 | 622 | 622 | 673 | [5 empty] | 4.59 | 14.74 | 96 | 35.004
LIT 225KV N0 1 MALINTRAT - SARRE | 17T0000000263027 | RTE | MALINTRAT | SARRE | 220 | 925 | 925 | 925 | 1080 | [5 empty] | 0.204 | 1.618 | 804.676 | 10.717
LIT 225kV N0 1 MALINTRAT-RULHAT | 17T000000026281Q | RTE | MALINTRAT | RULHAT | 220 | 1034 | 1149 | 1149 | 1244 | [5 empty] | 0.355 | 2.328 | 16.292 | 5.747
LIT 225kV N0 1 MAMBELIN - SAONE | 17T0000000263116 | RTE | MAMBELIN | SAONE | 220 | 801 | 930 | 930 | 1053 | [5 empty] | 2.786 | 17.707 | 129.49 | 44.648
LIT 225kV N0 1 MAMBELIN-PALENTE | 17T000000026308W | RTE | MAMBELIN | PALENTE | 220 | 577 | 706 | 706 | 782 | [5 empty] | 6.326 | 22.083 | 145.36 | 52.934
LIT 225kV N0 1 MAMBELIN-PONTARLIER | 17T000000026309U | RTE | MAMBELIN | PONTARLIER | 220 | 412 | 449 | 449 | 449 | [5 empty] | 9.519 | 35.036 | 243.446 | 86.68
LIT 225kV N0 1 MAMBELIN-PUSY | 17T0000000263108 | RTE | MAMBELIN | PUSY | 220 | 525 | 730 | 730 | 835 | [5 empty] | 6.231 | 31.693 | 219.17 | 77.914
LIT 225kV N0 1 MANOIR (LE)-ST-PIERRE-DE-BAILLEUL | 17T000000026349I | RTE | MANOIR (LE) | ST-PIERRE-DE-BAILLEUL | 220 | 757 | 946 | 946 | 1075 | [5 empty] | 2.544 | 16.971 | 119.226 | 41.848
LIT 225kV N0 1 MARGERIDE-PRATCLAUX | 17T0000000263969 | RTE | MARGERIDE | PRATCLAUX | 220 | 792 | 844 | 844 | 905 | [5 empty] | 3.738 | 15.121 | 111.884 | 38.458
LIT 225kV N0 1 MARGERIDE-RUEYRES | 17T0000000263977 | RTE | MARGERIDE | RUEYRES | 220 | 802 | 844 | 844 | 919 | [5 empty] | 4.645 | 19.038 | 135.938 | 47.388
LIT 225kV N0 1 MARMAGNE-VARENNES (-SUR-FOUZON) | 17T000000026440W | RTE | MARMAGNE | VARENNES (-SUR-FOUZON) | 220 | 409 | 644 | 644 | 761 | [5 empty] | 4.746 | 21.572 | 149.58 | 53.196
LIT 225kV N0 1 MARSILLON-PRAGNERES | 17T-FR-00000059M | RTE | MARSILLON | PRAGNERES | 220 | 565 | 673 | 673 | 765 | [5 empty] | 7.841 | 34.13 | 237.628 | 84.292
LIT 225kV N0 1 MARTYRE (LA)-SQUIVIDAN | 17T0000000264787 | RTE | MARTYRE (LA) | SQUIVIDAN | 220 | 1056 | 1123 | 1123 | 1189 | [5 empty] | 3.038 | 20.399 | 148.366 | 51.302
LIT 225kV N0 1 MASTAING-PERIZET (LE) | 17T000000026520Y | RTE | MASTAING | PERIZET (LE) | 220 | 975 | 1030 | 1030 | 1110 | [5 empty] | 2.219 | 10.244 | 71.288 | 24.738
LIT 225kV N0 1 MASTAING-PONT-SUR-SAMBRE | 17T000000026519J | RTE | MASTAING | PONT-SUR-SAMBRE | 220 | 975 | 976 | 1030 | 1104 | [5 empty] | 3.865 | 17.913 | 132.274 | 44.098
LIT 225kV N0 1 MAUBEUGE-PONT-SUR-SAMBRE | 17T000000026551N | RTE | MAUBEUGE | PONT-SUR-SAMBRE | 220 | 956 | 1010 | 1010 | 1088 | [5 empty] | 0.588 | 2.808 | 19.746 | 6.968
LIT 225kV N0 1 MAUGES (LES)-VERTOU | 17T0000000265589 | RTE | MAUGES (LES) | VERTOU | 220 | 488 | 682 | 682 | 795 | [5 empty] | 4.191 | 19.19 | 131.398 | 47.048
LIT 225kV N0 1 MAUREIX (LE)-PEYRAT-LE-CHATEAU | 17T0000000265872 | RTE | MAUREIX (LE) | PEYRAT-LE-CHATEAU | 220 | 725 | 800 | 800 | 865 | [5 empty] | 2.673 | 14.733 | 97.878 | 35.567
LIT 225kV N0 1 MERLATIERE - RECOUVRANCE | 17T0000000266771 | RTE | MERLATIERE | RECOUVRANCE | 220 | 870 | 870 | 1180 | 1180 | [5 empty] | 0.743 | 5.816 | 3282.96 | 35.439
LIT 225kV N0 1 MERLATIERE - SOULLANS | 17T000000026680C | RTE | MERLATIERE | SOULLANS | 220 | 1249 | 1337 | 1337 | 1434 | [5 empty] | 2.603 | 17.492 | 124.374 | 43.41
LIT 225kV N0 1 MEZEROLLES - PORCHEVILLE | 17T000000026726E | RTE | MEZEROLLES | PORCHEVILLE | 220 | 520 | 782 | 782 | 998 | [5 empty] | 0.371 | 2.449 | 17.688 | 6.148
LIT 225kV N0 1 MIONS-MOIRANS | 17T0000000267751 | RTE | MIONS | MOIRANS | 220 | 579 | 672 | 672 | 755 | [5 empty] | 5.95 | 27.53 | 184 | 67.808
LIT 225kV N0 1 MIONS-MOUCHE (LA) | 17T000000026777Y | RTE | MIONS | MOUCHE (LA) | 220 | 1800 | 2030 | 2030 | 2224 | [5 empty] | 0.42 | 4.24 | 52 | 13.7
LIT 225kV N0 1 MIONS-PONT-EVEQUE | 17T000000026778W | RTE | MIONS | PONT-EVEQUE | 220 | 880 | 992 | 992 | 1086 | [5 empty] | 1.22 | 8.32 | 54 | 18.949
LIT 225kV N0 1 MIONS-ST-VULBAS-EST | 17T0000000267808 | RTE | MIONS | ST-VULBAS-EST | 220 | 297 | 442 | 442 | 545 | [5 empty] | 3.84 | 14.24 | 90 | 33.6
LIT 225kV N0 1 MIONS-VENISSIEUX | 17T0000000267816 | RTE | MIONS | VENISSIEUX | 220 | 900 | 1015 | 1015 | 1112 | [5 empty] | 0.33 | 3.01 | 34 | 9.344
LIT 225kV N0 1 MITRY-MORY (E.D.F.)-SAUSSET | 17T0000000261334 | RTE | MITRY-MORY (E.D.F.) | SAUSSET | 220 | 731 | 835 | 835 | 930 | [5 empty] | 0.397 | 1.989 | 14.032 | 4.933
LIT 225kV N0 1 MITRY-MORY (E.D.F.)-VILLEVAUDE | 17T0000000261342 | RTE | MITRY-MORY (E.D.F.) | VILLEVAUDE | 220 | 899 | 984 | 984 | 1061 | [5 empty] | 0.727 | 3.391 | 23.734 | 8.375
LIT 225kV N0 1 MOIMONT - PLESSIS-GASSOT | 17T0000000268634 | RTE | MOIMONT | PLESSIS-GASSOT | 220 | 716 | 817 | 817 | 910 | [5 empty] | 0.867 | 4.462 | 40.258 | 10.848
LIT 225kV N0 1 MOLE (LA)-RUEYRES | 17T0000000268812 | RTE | MOLE (LA) | RUEYRES | 220 | 622 | 748 | 748 | 834 | [5 empty] | 7.221 | 34.122 | 221.894 | 81.267
LIT 225kV N0 1 MOLE (LA)-STE-FEYRE | 17T000000026902K | RTE | MOLE (LA) | STE-FEYRE | 220 | 578 | 694 | 694 | 774 | [5 empty] | 8.123 | 41.941 | 308.088 | 105.922
LIT 225kV N0 1 MONTCROISETTE-VENDIN | 17T000000027146R | RTE | MONTCROISETTE | VENDIN | 220 | 1273 | 1346 | 1346 | 1453 | [5 empty] | 0.293 | 1.942 | 14.134 | 4.88
LIT 225KV N0 1 MONTGROS - MONTPEZAT | 17T000000027183L | RTE | MONTGROS | MONTPEZAT | 220 | 370 | 559 | 559 | 695 | [5 empty] | 4.023 | 18.8 | 217.23 | 45.68
LIT 225KV N0 1 MONTGROS - PRATCLAUX | 17T000000027184J | RTE | MONTGROS | PRATCLAUX | 220 | 346 | 524 | 524 | 649 | [5 empty] | 1.973 | 9.26 | 164.732 | 22.994
LIT 225kV N0 1 MONTLUCON-MONTVICQ | 17T000000027193I | RTE | MONTLUCON | MONTVICQ | 220 | 555 | 692 | 692 | 790 | [5 empty] | 1.752 | 7.035 | 48.486 | 17.28
LIT 225kV N0 1 MONTOIS-SAINT HUBERT | 17T000000027223Z | RTE | MONTOIS | SAINT HUBERT | 220 | 456 | 556 | 556 | 634 | [5 empty] | 1.92 | 6.187 | 39.3 | 14.58
LIT 225kV N0 1 MONTPELLIER - TAMAREAU | 17T000000027227R | RTE | MONTPELLIER | TAMAREAU | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 1.217 | 8.128 | 58.594 | 20.339
LIT 225kV N0 1 MONTPEZAT-PRATCLAUX | 17T000000027234U | RTE | MONTPEZAT | PRATCLAUX | 220 | 346 | 524 | 524 | 649 | [5 empty] | 5.976 | 26.796 | 186.16 | 66.141
LIT 225kV N0 1 MORBRAS-VILLENEUVE-ST-GEORGES | 17T0000000269428 | RTE | MORBRAS | VILLENEUVE-ST-GEORGES | 220 | 886 | 886 | 984 | 1061 | [5 empty] | 1.37 | 6.904 | 149.642 | 18.381
LIT 225kV N0 1 MOUGINS-PLAN-DE-GRASSE | 17T000000027028X | RTE | MOUGINS | PLAN-DE-GRASSE | 220 | 1000 | 1000 | 1160 | 1185 | [5 empty] | 0.584 | 4.203 | 130.156 | 12.987
LIT 225kV N0 1 MOULINEAUX - VILLEJUST | 17T0000000270414 | RTE | MOULINEAUX | VILLEJUST | 220 | 750 | 750 | 1030 | 1030 | [5 empty] | 0.581 | 5.531 | 337.586 | 21.407
LIT 225kV N0 1 MUREAUX (LES) - NOUROTTES | 17T000000027278A | RTE | MUREAUX (LES) | NOUROTTES | 220 | 1172 | 1172 | 1285 | 1388 | [5 empty] | 0.687 | 4.587 | 44.24 | 11.647
LIT 225kV N0 1 NEMOURS-VILLEMANDEUR | 17T0000000273875 | RTE | NEMOURS | VILLEMANDEUR | 220 | 520 | 782 | 782 | 998 | [5 empty] | 1.682 | 11.498 | 81.952 | 28.561
LIT 225kV N0 1 NEOULES-VINS | 17T000000027393A | RTE | NEOULES | VINS | 220 | 1057 | 1057 | 1160 | 1224 | [5 empty] | 1.669 | 11.088 | 91.806 | 27.764
LIT 225kV N0 1 NIORT - VAL-DE-SEVRE | 17T000000027437G | RTE | NIORT | VAL-DE-SEVRE | 220 | 803 | 858 | 858 | 918 | [5 empty] | 6.196 | 22.472 | 146.658 | 52.463
LIT 225kV N0 1 NOGENTEL-ORMES | 17T000000027439C | RTE | NOGENTEL | ORMES | 220 | 1172 | 1285 | 1285 | 1375 | [5 empty] | 3.502 | 23.311 | 169.074 | 57.945
LIT 225kV N0 1 ONET-LE-CHATEAU-RUEYRES | 17T000000027503T | RTE | ONET-LE-CHATEAU | RUEYRES | 220 | 902 | 1004 | 1004 | 1131 | [5 empty] | 2.935 | 20.096 | 142.952 | 49.985
LIT 225kV N0 1 ORANGERIE (L) - MONDION | 17T0000000269177 | RTE | MONDION | ORANGERIE (L) | 220 | 957 | 1023 | 1023 | 1096 | [5 empty] | 1.277 | 5.906 | 41.332 | 14.139
LIT 225kV N0 1 PALENTE -SAONE | 17T000000027947U | RTE | PALENTE | SAONE | 220 | 928 | 1001 | 1001 | 1096 | [5 empty] | 0.565 | 3.201 | 22.83 | 7.958
LIT 225kV N0 1 PALUN (LA) - SAINTE-TULLE 1 | 17T000000027983Q | RTE | PALUN (LA) | STE-TULLE | 220 | 816 | 889 | 889 | 947 | [5 empty] | 3.511 | 18.486 | 130.564 | 45.834
LIT 225kV N0 1 PALUN (LA)-SEPTEMES | 17T000000027982S | RTE | PALUN (LA) | SEPTEMES | 220 | 1375 | 1437 | 1437 | 1500 | [5 empty] | 0.524 | 6.439 | 48.208 | 16.137
LIT 225kV N0 1 PASSY-PRESSY | 17T000000028001B | RTE | PASSY | PRESSY | 220 | 619 | 687 | 687 | 744 | [5 empty] | 2.315 | 10.285 | 79.89 | 26.303
LIT 225kV N0 1 PATIS - REMISE | 17T0000000280053 | RTE | PATIS | REMISE | 220 | 1035 | 1035 | 1235 | 1235 | [5 empty] | 1.164 | 7.763 | 95.542 | 19.879
LIT 225kV N0 1 PELISSIER-ST-VICTOR | 17T0000000280207 | RTE | PELISSIER | ST-VICTOR | 220 | 1018 | 1117 | 1117 | 1213 | [5 empty] | 3.91 | 22.5 | 162 | 55.118
LIT 225kV N0 1 PERIZET (LE)-SETIER | 17T000000028083K | RTE | PERIZET (LE) | SETIER | 220 | 579 | 709 | 709 | 822 | [5 empty] | 2.404 | 11.2 | 74.746 | 27.058
LIT 225kV N0 1 PERTAIN-ROYE | 17T0000000280995 | RTE | PERTAIN | ROYE | 220 | 566 | 692 | 692 | 802 | [5 empty] | 1.083 | 4.936 | 50.362 | 12.168
LIT 225kV N0 1 PESSAC-SAUCATS | 17T000000028124W | RTE | PESSAC | SAUCATS | 220 | 938 | 980 | 1055 | 1132 | [5 empty] | 1.234 | 8.332 | 61.976 | 21.293
LIT 225kV N0 1 PETITE-ROSSELLE-SARREGUEMINES | 17T0000000278346 | RTE | PETITE-ROSSELLE | SARREGUEMINES | 220 | 843 | 909 | 909 | 996 | [5 empty] | 1.985 | 10.313 | 72.966 | 24.575
LIT 225kV N0 1 PETITE-ROSSELLE-ST-AVOLD | 17T0000000278354 | RTE | PETITE-ROSSELLE | ST-AVOLD | 220 | 715 | 715 | 840 | 840 | [5 empty] | 1.424 | 6.322 | 62.858 | 15.83
LIT 225kV N0 1 PIERRETTE (LA) - VERTEFEUILLE | 17T000000028370H | RTE | PIERRETTE (LA) | VERTEFEUILLE | 220 | 825 | 825 | 990 | 990 | [5 empty] | 0.951 | 4.24 | 35.98 | 10.423
LIT 225kV N0 1 PLAINE HAUTE-ROSPEZ | 17T0000000277439 | RTE | PLAINE HAUTE | ROSPEZ | 220 | 1375 | 1437 | 1437 | 1484 | [5 empty] | 3.275 | 21.742 | 158.086 | 54.579
LIT 225kV N0 1 PLAINE HAUTE-TREGUEUX | 17T0000000277447 | RTE | PLAINE HAUTE | TREGUEUX | 220 | 1212 | 1262 | 1262 | 1318 | [5 empty] | 0.835 | 5.58 | 40.16 | 13.973
LIT 225kV N0 1 PLAISANCE-ROMAINVILLE | 17T000000028164K | RTE | PLAISANCE | ROMAINVILLE | 220 | 480 | 480 | 835 | 835 | [5 empty] | 0.393 | 2.335 | 343.79 | 7.921
LIT 225kV N0 1 PLAN-D ORGON - ROQUEROUSSE | 17T000000027795R | RTE | PLAN-D ORGON | ROQUEROUSSE | 220 | 816 | 889 | 889 | 947 | [5 empty] | 1.755 | 8.022 | 55.316 | 19.64
LIT 225kV N0 1 PLESSIS-GASSOT - SAUSSET | 17T0000000276807 | RTE | PLESSIS-GASSOT | SAUSSET | 220 | 899 | 984 | 984 | 1061 | [5 empty] | 1.154 | 5.691 | 40.022 | 14.028
LIT 225kV N0 1 PLESSIS-GASSOT - SEINE | 17T0000000276815 | RTE | PLESSIS-GASSOT | SEINE | 220 | 888 | 950 | 972 | 1049 | [5 empty] | 1.303 | 6.855 | 68.972 | 17.062
LIT 225kV N0 1 PONTARLIER - SAONE | 17T000000028372D | RTE | PONTARLIER | SAONE | 220 | 412 | 420 | 420 | 420 | [5 empty] | 6.401 | 17.196 | 114.646 | 41.663
LIT 225kV N0 1 PONTEAU - REALTOR | 17T000000028217P | RTE | PONTEAU | REALTOR | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 1.009 | 10.357 | 126.436 | 34.309
LIT 225kV N0 1 PONT-SEPT-SAINNEVILLE | 17T000000027876R | RTE | PONT-SEPT | SAINNEVILLE | 220 | 455 | 455 | 560 | 560 | [5 empty] | 0.62 | 3.468 | 275.832 | 11.365
LIT 225kV N0 1 PONT-SEPT-SANDOUVILLE | 17T000000027877P | RTE | PONT-SEPT | SANDOUVILLE | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 0.877 | 5.875 | 42.038 | 14.613
LIT 225kV N0 1 PORCHEVILLE-PUISEUX | 17T000000028249C | RTE | PORCHEVILLE | PUISEUX | 220 | 511 | 768 | 768 | 979 | [5 empty] | 1.381 | 9.031 | 65.39 | 22.686
LIT 225kV N0 1 PORCHEVILLE-ST-PIERRE-DE-BAILLEUL | 17T000000028250R | RTE | PORCHEVILLE | ST-PIERRE-DE-BAILLEUL | 220 | 1140 | 1248 | 1248 | 1347 | [5 empty] | 2.91 | 19.42 | 136.114 | 48.359
LIT 225kV N0 1 PORTET-ST-SIMON - RIVENEUVE | 17T000000027902F | RTE | PORTET-ST-SIMON | RIVENEUVE | 220 | 813 | 890 | 890 | 966 | [5 empty] | 4.996 | 22.853 | 150.496 | 54.76
LIT 225kV N0 1 PORTET-ST-SIMON - ST-ORENS | 17T000000027903D | RTE | PORTET-ST-SIMON | ST-ORENS | 220 | 780 | 780 | 940 | 940 | [5 empty] | 0.722 | 4.696 | 57.668 | 11.937
LIT 225kV N0 1 PORTET-ST-SIMON -TARASCON | 17T000000027904B | RTE | PORTET-ST-SIMON | TARASCON | 220 | 430 | 550 | 550 | 630 | [5 empty] | 7.159 | 32.6 | 223.94 | 79.654
LIT 225kV N0 1 PORT-JEROME-SANDOUVILLE | 17T000000027784W | RTE | PORT-JEROME | SANDOUVILLE | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 1.336 | 8.951 | 64.138 | 22.28
LIT 225kV N0 1 PORT-JEROME-VAUPALIERE (LA) | 17T000000027785U | RTE | PORT-JEROME | VAUPALIERE (LA) | 220 | 618 | 745 | 745 | 819 | [5 empty] | 3.64 | 16.84 | 122 | 41.042
LIT 225kV N0 1 POTEAU-ROUGE - SQUIVIDAN | 17T000000027840B | RTE | POTEAU-ROUGE | SQUIVIDAN | 220 | 1280 | 1332 | 1332 | 1382 | [5 empty] | 3.689 | 24.528 | 177.72 | 61.476
LIT 225kV N0 1 POTEAU-ROUGE - THEIX | 17T0000000278419 | RTE | POTEAU-ROUGE | THEIX | 220 | 1212 | 1262 | 1262 | 1318 | [5 empty] | 3.166 | 21.043 | 152.728 | 52.773
LIT 225kV N0 1 PRATCLAUX - TREVAS | 17T000000028299Y | RTE | PRATCLAUX | TREVAS | 220 | 1059 | 1141 | 1141 | 1215 | [5 empty] | 3.554 | 21.054 | 157.316 | 53.845
LIT 225kV N0 1 PRATCLAUX-SANSSAC (L'EGLISE) | 17T0000000282971 | RTE | PRATCLAUX | SANSSAC (L'EGLISE) | 220 | 639 | 717 | 717 | 860 | [5 empty] | 1.338 | 6.033 | 41.358 | 14.685
LIT 225kV N0 1 PRAZ-ST-ANDRE-SAUSSAZ II (LA) | 17T0000000276289 | RTE | PRAZ-ST-ANDRE | SAUSSAZ II (LA) | 220 | 966 | 1076 | 1076 | 1168 | [5 empty] | 0.68 | 3.98 | 28 | 9.854
LIT 225kV N0 1 PREGUILLAC - SAINTES | 17T000000028328G | RTE | PREGUILLAC | SAINTES | 220 | 1180 | 1310 | 1310 | 1390 | [5 empty] | 0.668 | 4.489 | 51.048 | 11.329
LIT 225kV N0 1 PRELES (LES)-SEREIN | 17T000000028332P | RTE | PRELES (LES) | SEREIN | 220 | 1100 | 1187 | 1187 | 1302 | [5 empty] | 0.842 | 5.611 | 40.562 | 13.94
LIT 225kV N0 1 PUSY-ROLAMPONT | 17T000000028408I | RTE | PUSY | ROLAMPONT | 220 | 827 | 891 | 891 | 976 | [5 empty] | 6.717 | 30.544 | 205.832 | 74.096
LIT 225kV N0 1 PYMONT-VOUGLANS | 17T000000028421Q | RTE | PYMONT | VOUGLANS | 220 | 704 | 866 | 866 | 990 | [5 empty] | 2.284 | 14.652 | 108.086 | 37.473
LIT 225KV N0 1 QUATRE SEIGNEURS - SAUMAD | 17T000000028442I | RTE | QUATRE-SEIGNEURS | SAUMADE | 220 | 1100 | 1100 | 1300 | 1300 | [5 empty] | 0.086 | 1.147 | 700.826 | 7.8
LIT 225kV N0 1 QUATRE SEIGNEURS - TAMAREAU | 17T000000028443G | RTE | QUATRE-SEIGNEURS | TAMAREAU | 220 | 855 | 855 | 1040 | 1040 | [5 empty] | 0.684 | 4.549 | 59.886 | 11.66
LIT 225kV N0 1 QUINTES (LES)-ST-CALAIS | 17T0000000284559 | RTE | QUINTES (LES) | ST-CALAIS | 220 | 1249 | 1316 | 1316 | 1389 | [5 empty] | 2.354 | 15.737 | 112.456 | 39.236
LIT 225kV N0 1 RAIE-TORTUE - VILLEJUST | 17T000000028486Z | RTE | RAIE-TORTUE | VILLEJUST | 220 | 1040 | 1285 | 1285 | 1388 | [5 empty] | 0.478 | 4.652 | 63.038 | 15.924
LIT 225kV N0 1 RASSUEN-ROQUEROUSSE | 17T000000028532H | RTE | RASSUEN | ROQUEROUSSE | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 1.76 | 12.056 | 89.09 | 30.192
LIT 225kV N0 1 REALTOR-SEPTEMES | 17T000000028535B | RTE | REALTOR | SEPTEMES | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 0.413 | 2.766 | 19.808 | 6.966
LIT 225kV N0 1 RICHEMONT-SAINT HUBERT | 17T0000000286551 | RTE | RICHEMONT | SAINT HUBERT | 220 | 413 | 714 | 714 | 899 | [5 empty] | 0.254 | 1.501 | 10.762 | 3.77
LIT 225kV N0 1 RIVENEUVE-TARASCON | 17T000000028688N | RTE | RIVENEUVE | TARASCON | 220 | 716 | 807 | 807 | 887 | [5 empty] | 3.286 | 14.921 | 99.186 | 35.577
LIT 225kV N0 1 RIVIERE (LA) - SANSSAC (L'EGLISE) | 17T000000028692W | RTE | RIVIERE (LA) | SANSSAC (L'EGLISE) | 220 | 900 | 900 | 1100 | 1100 | [5 empty] | 4.186 | 25.175 | 778.132 | 69.448
LIT 225kV N0 1 RIVIERE (LA)-TREVAS | 17T000000028693U | RTE | RIVIERE (LA) | TREVAS | 220 | 639 | 717 | 717 | 783 | [5 empty] | 2.465 | 11.382 | 73.966 | 27.117
LIT 225kV N0 1 ROGNAC-ROQUEROUSSE | 17T0000000287256 | RTE | ROGNAC | ROQUEROUSSE | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 1.492 | 10.006 | 69.744 | 24.566
LIT 225kV N0 1 ROGNAC-ST-CHAMAS | 17T0000000287264 | RTE | ROGNAC | ST-CHAMAS | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 0.848 | 5.624 | 40.928 | 14.043
LIT 225kV N0 1 ROMAINVILLE-VILLEVAUDE | 17T000000028731B | RTE | ROMAINVILLE | VILLEVAUDE | 220 | 480 | 480 | 782 | 835 | [5 empty] | 1.394 | 7.184 | 369.73 | 20.202
LIT 225kV N0 1 ROQUEROUSSE-ST-ESTEVE | 17T000000028811D | RTE | ROQUEROUSSE | ST-ESTEVE | 220 | 1034 | 1128 | 1128 | 1203 | [5 empty] | 1.439 | 9.427 | 65.78 | 23.308
LIT 225kV N0 1 ROUGEMONTIER-YAINVILLE | 17T000000028765V | RTE | ROUGEMONTIER | YAINVILLE | 220 | 757 | 946 | 946 | 1075 | [5 empty] | 1.618 | 10.872 | 76.628 | 26.893
LIT 225kV N0 1 ROUSSON-SEREIN | 17T000000028778M | RTE | ROUSSON | SEREIN | 220 | 435 | 595 | 595 | 680 | [5 empty] | 3.821 | 17.297 | 119.928 | 42.58
LIT 225kV N0 1 RUEYRES-SAVIGNAC | 17T0000000288139 | RTE | RUEYRES | SAVIGNAC | 220 | 548 | 606 | 606 | 678 | [5 empty] | 5.109 | 19.887 | 125.394 | 45.79
LIT 225KV N0 1 SACLAY (PLATEAU) - VILLERAS | 17T000000028858O | RTE | SACLAY (PLATEAU) | VILLERAS | 220 | 540 | 540 | 540 | 600 | [5 empty] | 0.171 | 0.865 | 322.234 | 5.103
LIT 225kV N0 1 SAINNEVILLE-YAINVILLE | 17T000000028882R | RTE | SAINNEVILLE | YAINVILLE | 220 | 769 | 872 | 872 | 961 | [5 empty] | 4.38 | 19.966 | 143.35 | 49.27
LIT 225kV N0 1 SANILHAC-TUILIERES | 17T000000028895I | RTE | SANILHAC | TUILIERES | 220 | 289 | 543 | 543 | 682 | [5 empty] | 4.218 | 19.176 | 131.02 | 46.667
LIT 225kV N0 1 SAUSSET-VILLEVAUDE | 17T000000028935W | RTE | SAUSSET | VILLEVAUDE | 220 | 750 | 850 | 850 | 895 | [5 empty] | 0.985 | 4.45 | 31.062 | 11.001
LIT 225kV N0 1 SAUVETERRE-DE-GUYENNE - PIQUAGE A FONCROSE |  | RTE | SAUVETERRE-DE-GUYENNE | PIQUAGE A FONCROSE | 220 | 85 | 85 | 85 | 85 | [5 empty] | 0.041 | 0.125 | 36.084 | 0.7
LIT 225kV N0 1 SEREIN-TONNERRE | 17T0000000290024 | RTE | SEREIN | TONNERRE | 220 | 1100 | 1187 | 1187 | 1302 | [5 empty] | 1.393 | 9.486 | 65.592 | 23.15
LIT 225kV N0 1 SERRE-PONCON-SISTERON | 17T0000000288511 | RTE | SERRE-PONCON | SISTERON | 220 | 862 | 928 | 928 | 987 | [5 empty] | 3.508 | 16.913 | 119.666 | 42.224
LIT 225kV N0 1 SERRIERES-ST-VULBAS-EST | 17T000000029007V | RTE | SERRIERES | ST-VULBAS-EST | 220 | 204 | 397 | 397 | 493 | [5 empty] | 6.685 | 21.696 | 133.782 | 50.471
LIT 225kV N0 1 SOLEIL (LE)-VOLVON | 17T000000029043R | RTE | SOLEIL (LE) | VOLVON | 220 | 1123 | 1211 | 1211 | 1290 | [5 empty] | 0.897 | 5.987 | 43.11 | 14.948
LIT 225kV N0 1 ST CESAIRE - ST CHRISTOL | 17T000000029164F | RTE | ST-CESAIRE | ST-CHRISTOL | 220 | 597 | 676 | 676 | 724 | [5 empty] | 3.42 | 11.744 | 72.012 | 27.156
LIT 225kV N0 1 ST-AUBAN-STE-TULLE | 17T0000000291004 | RTE | ST-AUBAN | STE-TULLE | 220 | 1123 | 1201 | 1201 | 1268 | [5 empty] | 5.042 | 18.112 | 112.99 | 42.091
LIT 225kV N0 1 ST-AUBIN-VERSAILLES | 17T0000000290966 | RTE | ST-AUBIN | VERSAILLES | 220 | 673 | 673 | 826 | 826 | [5 empty] | 0.412 | 1.313 | 634.936 | 10.815
LIT 225kV N0 1 ST-AVOLD-VIGY | 17T000000029129H | RTE | ST-AVOLD | VIGY | 220 | 1412 | 1412 | 1639 | 1639 | [5 empty] | 0.723 | 9.937 | 148.83 | 32.825
LIT 225kV N0 1 ST-ELOI - VIGNOL | 17T0000000291792 | RTE | ST-ELOI | VIGNOL | 220 | 617 | 740 | 740 | 826 | [5 empty] | 5.403 | 26.383 | 177.894 | 63.891
LIT 225kV N0 1 ST-ESTEVE-SAINTE-TULLE 1 | 17T000000029181F | RTE | ST-ESTEVE | STE-TULLE | 220 | 280 | 647 | 647 | 824 | [5 empty] | 1.993 | 13.509 | 100.14 | 34.371
LIT 225kV N0 1 ST-JULIEN-VIGY | 17T000000029219G | RTE | ST-JULIEN | VIGY | 220 | 1100 | 1187 | 1187 | 1302 | [5 empty] | 0.433 | 2.901 | 20.774 | 7.202
LIT 225kV N0 1 ST-ORENS-VERFEIL | 17T0000000292578 | RTE | ST-ORENS | VERFEIL | 220 | 1080 | 1185 | 1185 | 1289 | [5 empty] | 1.057 | 7.079 | 50.728 | 17.61
LIT 225kV N0 1 TAVEL - VIRADEL | 17T0000000293655 | RTE | TAVEL | VIRADEL | 220 | 985 | 985 | 1129 | 1165 | [5 empty] | 2.891 | 18.245 | 173.838 | 46.486
LIT 225kV N0 1 VAUPALIERE (LA)-YAINVILLE | 17T000000029522F | RTE | VAUPALIERE (LA) | YAINVILLE | 220 | 599 | 746 | 746 | 847 | [5 empty] | 1.433 | 6.577 | 59.196 | 16.018
LIT 225kV N0 1 VERTEFEUILLE-WEPPES | 17T000000029539Z | RTE | VERTEFEUILLE | WEPPES | 220 | 1273 | 1346 | 1346 | 1453 | [5 empty] | 0.758 | 5.074 | 36.432 | 12.642
LIT 225kV N0 1 VINCEY-VITTEL | 17T000000029541B | RTE | VINCEY | VITTEL | 220 | 881 | 964 | 964 | 1040 | [5 empty] | 2.119 | 14.104 | 101.88 | 35.257
LIT 225kV N0 2 ALLINGES-CORNIER | 17T000000015398G | RTE | ALLINGES | CORNIER | 220 | 966 | 1076 | 1076 | 1168 | [5 empty] | 2.42 | 14.474 | 108.052 | 36.992
LIT 225kV N0 2 AQUEDUCS (LES)-CIROLLIERS | 17T0000000157875 | RTE | AQUEDUCS (LES) | CIROLLIERS | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 0.551 | 3.674 | 26.512 | 9.206
LIT 225kV N0 2 ARDOISE (L )-TAVEL | 17T0000000158685 | RTE | ARDOISE (L ) | TAVEL | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 0.649 | 4.346 | 31.182 | 10.815
LIT 225kV N0 2 ARGIA (BAYONNE SUD)-MOUGUERRE | 17T-FR-00000062X | RTE | ARGIA (BAYONNE SUD) | MOUGUERRE | 220 | 635 | 635 | 870 | 870 | [5 empty] | 0.382 | 2.65 | 179.556 | 7.966
LIT 225kV N0 2 ARNAGE-QUINTES (LES) | 17T0000000160716 | RTE | ARNAGE | QUINTES (LES) | 220 | 1032 | 1124 | 1124 | 1212 | [5 empty] | 0.328 | 2.216 | 16.414 | 5.558
LIT 225kV N0 2 ARRIGHI-CHARENTON | 17T000000016191X | RTE | ARRIGHI | CHARENTON | 220 | 220 | 220 | 340 | 340 | [5 empty] | 0.139 | 0.473 | 411.802 | 4.473
LIT 225kV N0 2 ARRIGHI-MORBRAS | 17T000000016192V | RTE | ARRIGHI | MORBRAS | 220 | 1980 | 2008 | 2250 | 2420 | [5 empty] | 0.665 | 6.133 | 133.126 | 22.198
LIT 225kV N0 2 BALMA (POSTE)-VERFEIL | 17T000000017147V | RTE | BALMA (POSTE) | VERFEIL | 220 | 1080 | 1185 | 1185 | 1289 | [5 empty] | 0.944 | 6.329 | 45.32 | 15.741
LIT 225kV N0 2 BEAUMONT-MONTEUX-GAMPALOUP | 17T000000016944A | RTE | BEAUMONT-MONTEUX | GAMPALOUP | 220 | 880 | 992 | 992 | 1086 | [5 empty] | 2.17 | 14.7 | 104 | 36.312
LIT 225kV N0 2 BEAUTOR (POSTE)-LATENA | 17T000000019064P | RTE | BEAUTOR (POSTE) | LATENA | 220 | 1400 | 1500 | 1500 | 1550 | [5 empty] | 0.95 | 9.241 | 125.394 | 31.657
LIT 225KV N0 2 BEC - MARQUIS (LE) | 17T000000017468B | RTE | BEC | MARQUIS (LE) | 220 | 490 | 490 | 490 | 580 | [5 empty] | 0.267 | 1.165 | 39.668 | 4.807
LIT 225kV N0 2 BEZAUMONT-VANDIERES | 17T0000000177914 | RTE | BEZAUMONT | VANDIERES | 220 | 1172 | 1285 | 1285 | 1375 | [5 empty] | 0.817 | 5.428 | 39.396 | 13.741
LIT 225KV N0 2 BEZIERS-EST - ST-VINCENT | 17T0000000177582 | RTE | BEZIERS-EST | ST-VINCENT | 220 | 419 | 419 | 419 | 567 | [5 empty] | 0.259 | 0.761 | 229.032 | 4.443
LIT 225kV N0 2 BOISSE (LA) - CUSSET-POSTE | 17T0000000181128 | RTE | BOISSE (LA) | CUSSET-POSTE | 220 | 857 | 857 | 1024 | 1024 | [5 empty] | 0.63 | 4.83 | 80 | 12.768
LIT 225kV N0 2 BOISSE (LA) - MIONS | 17T0000000181136 | RTE | BOISSE (LA) | MIONS | 220 | 900 | 1015 | 1015 | 1112 | [5 empty] | 1.16 | 8.01 | 78 | 20.131
LIT 225kV N0 2 BOLLENE - TRICASTIN-POSTE (LE) | 17T000000018182O | RTE | BOLLENE (POSTE RESEAU) | TRICASTIN-POSTE (LE) | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 0.344 | 2.304 | 16.462 | 5.733
LIT 225kV N0 2 BONNEAU-VALDIVIENNE | 17T000000018197B | RTE | BONNEAU | VALDIVIENNE | 220 | 1180 | 1310 | 1310 | 1390 | [5 empty] | 1.653 | 10.436 | 84.588 | 27.592
LIT 225kV N0 2 BROC-CARROS (LE) - LINGOSTIERE | 17T000000016756B | RTE | BROC-CARROS (LE) | LINGOSTIERE | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 0.715 | 4.787 | 34.358 | 11.928
LIT 225kV N0 2 BROC-CARROS (LE) - TRINITE-VICTOR | 17T0000000167579 | RTE | BROC-CARROS (LE) | TRINITE-VICTOR | 220 | 1062 | 1081 | 1160 | 1207 | [5 empty] | 0.812 | 5.544 | 40.342 | 13.937
LIT 225kV N0 2 CANTEGRIT-NAOUTOT | 17T0000000195564 | RTE | CANTEGRIT | NAOUTOT | 220 | 845 | 925 | 925 | 1005 | [5 empty] | 2.188 | 14.696 | 103.742 | 36.79
LIT 225kV N0 2 CARRIERES-TERRIER | 17T000000019679P | RTE | CARRIERES | TERRIER | 220 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.454 | 4.265 | 61.608 | 15.648
LIT 225kV N0 2 CAZARIL-LANNEMEZAN | 17T000000019787M | RTE | CAZARIL | LANNEMEZAN | 220 | 1018 | 1117 | 1117 | 1213 | [5 empty] | 0.776 | 4.67 | 33.994 | 11.751
LIT 225kV N0 2 CERNAY-VESLE | 17T0000000199055 | RTE | CERNAY | VESLE | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 1.051 | 7.006 | 50.634 | 17.55
LIT 225kV N0 2 CHAINGY - DAMBRON | 17T000000020069H | RTE | CHAINGY | DAMBRON | 220 | 888 | 983 | 983 | 1042 | [5 empty] | 2.522 | 11.141 | 70.926 | 26.253
LIT 225kV N0 2 CHALON-GROSNE | 17T0000000201109 | RTE | CHALON | GROSNE | 220 | 1400 | 1500 | 1500 | 1550 | [5 empty] | 0.752 | 7.047 | 102.744 | 25.07
LIT 225kV N0 2 CHAMPAGNIER - EYBENS | 17T000000021409E | RTE | CHAMPAGNIER | EYBENS | 220 | 1014 | 1014 | 1178 | 1191 | [5 empty] | 0.517 | 3.368 | 24.452 | 8.569
LIT 225kV N0 2 CHAMPS-REGNAUD-VIELMOULIN | 17T000000019344J | RTE | CHAMPS-REGNAUD | VIELMOULIN | 220 | 847 | 865 | 985 | 1060 | [5 empty] | 2.005 | 13.363 | 105.722 | 33.8
LIT 225kV N0 2 CHANCENAY-REVIGNY | 17T000000020169D | RTE | CHANCENAY | REVIGNY | 220 | 1172 | 1285 | 1285 | 1375 | [5 empty] | 0.977 | 6.515 | 47.09 | 16.24
LIT 225kV N0 2 CHATEAU-GOMBERT - ENCO-DE-BOTTE | 17T0000000192014 | RTE | CHATEAU-GOMBERT | ENCO-DE-BOTTE | 220 | 438 | 438 | 438 | 438 | [5 empty] | 0.337 | 1.122 | 343.364 | 6.355
LIT 225kV N0 2 CHATEAUNEUF-DU-RHONE-LOGIS-NEUF | 17T0000000193588 | RTE | CHATEAUNEUF-DU-RHONE | LOGIS-NEUF | 220 | 862 | 928 | 928 | 987 | [5 empty] | 2.742 | 12.439 | 92.21 | 30.035
LIT 225kV N0 2 CHESNOY (LE)-COURTRY | 17T000000020410Y | RTE | CHESNOY (LE) | COURTRY | 220 | 920 | 920 | 1100 | 1100 | [5 empty] | 1.181 | 7.961 | 89.606 | 20.002
LIT 225kV N0 2 CHOLET-DISTRE | 17T0000000205647 | RTE | CHOLET | DISTRE | 220 | 957 | 1023 | 1023 | 1096 | [5 empty] | 7.299 | 36.334 | 255.236 | 89.929
LIT 225kV N0 2 CHOOZ-MAZURES | 17T000000020577Z | RTE | CHOOZ | MAZURES | 220 | 843 | 909 | 909 | 996 | [5 empty] | 0.759 | 9.395 | 110.56 | 29.849
LIT 225kV N0 2 CIROLLIERS - LOGES (LES) | 17T000000020613K | RTE | CIROLLIERS | LOGES (LES) | 220 | 880 | 880 | 1130 | 1130 | [5 empty] | 0.377 | 2.555 | 69.642 | 7.205
LIT 225kV N0 2 CLEON-GRAND-COURONNE | 17T000000020724B | RTE | CLEON | GRAND-COURONNE | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 0.329 | 2.198 | 15.816 | 5.473
LIT 225kV N0 2 COQUAINVILLIERS-ROUGEMONTIER | 17T000000021046O | RTE | COQUAINVILLIERS | ROUGEMONTIER | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 2.765 | 18.62 | 131.728 | 46.234
LIT 225kV N0 2 CORBIERE (LA)-DISTRE | 17T000000021143Q | RTE | CORBIERE (LA) | DISTRE | 220 | 1249 | 1337 | 1337 | 1434 | [5 empty] | 2.745 | 18.496 | 130.838 | 45.808
LIT 225kV N0 2 CORDEMAIS-POSTE-PONTCHATEAU | 17T000000021053R | RTE | CORDEMAIS-POSTE | PONTCHATEAU | 220 | 1249 | 1337 | 1337 | 1432 | [5 empty] | 1.421 | 9.618 | 71.296 | 24.461
LIT 225kV N0 2 CORNIER-GENISSIAT-POSTE | 17T000000021172J | RTE | CORNIER | GENISSIAT-POSTE | 220 | 396 | 660 | 660 | 830 | [5 empty] | 2.437 | 15.786 | 114.206 | 39.423
LIT 225kV N0 2 COUDON (LE)-NEOULES | 17T0000000212767 | RTE | COUDON (LE) | NEOULES | 220 | 1001 | 1093 | 1093 | 1165 | [5 empty] | 1.096 | 6.601 | 47.942 | 16.604
LIT 225kV N0 2 CRECHETS (LES)-WEPPES | 17T000000021489R | RTE | CRECHETS (LES) | WEPPES | 220 | 810 | 810 | 945 | 945 | [5 empty] | 0.872 | 5.815 | 57.278 | 14.426
LIT 225kV N0 2 DARSE-FEUILLANE | 17T000000022134M | RTE | DARSE | FEUILLANE | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 0.725 | 4.838 | 44.142 | 13.766
LIT 225kV N0 2 DRONNIERE (LA) - TOURBE | 17T000000022488O | RTE | DRONNIERE (LA) | TOURBE | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 0.615 | 4.098 | 29.62 | 10.55
LIT 225kV N0 2 ECHALAS - GIVORS | 17T0000000226067 | RTE | ECHALAS | GIVORS | 220 | 900 | 910 | 1015 | 1080 | [5 empty] | 0.42 | 2.89 | 44 | 7.034
LIT 225kV N0 2 ENCO-DE-BOTTE-PALUN (LA) | 17T0000000225354 | RTE | ENCO-DE-BOTTE | PALUN (LA) | 220 | 1001 | 1093 | 1093 | 1165 | [5 empty] | 1.123 | 7.058 | 51.558 | 17.816
LIT 225kV N0 2 FALLOU -PIQUAGE A VILLIERS-LE-BEL | 17T0000000231494 | RTE | FALLOU | PIQUAGE A VILLIERS-LE-BEL | 220 | 930 | 930 | 1050 | 1050 | [5 empty] | 0.934 | 6.191 | 82.924 | 16.184
LIT 225kV N0 2 FALLOU-NOVION | 17T0000000231478 | RTE | FALLOU | NOVION | 220 | 935 | 935 | 1105 | 1105 | [5 empty] | 0.106 | 0.916 | 358.304 | 5.478
LIT 225kV N0 2 FEUILLANE - PONTEAU | 17T000000023267Z | RTE | FEUILLANE | PONTEAU | 220 | 835 | 835 | 913 | 913 | [5 empty] | 0.555 | 5.856 | 71.412 | 19.037
LIT 225kV N0 2 FOUSCAIS - TAMAREAU | 17T0000000235309 | RTE | FOUSCAIS | TAMAREAU | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 1.495 | 9.985 | 71.814 | 24.908
LIT 225kV N0 2 FREJUS-TRANS | 17T000000023589D | RTE | FREJUS | TRANS | 220 | 1062 | 1066 | 1160 | 1238 | [5 empty] | 1.397 | 9.218 | 95.876 | 22.8
LIT 225kV N0 2 GINESTOUS-LESQUIVE | 17T000000024188Q | RTE | GINESTOUS | LESQUIVE | 220 | 1080 | 1185 | 1185 | 1289 | [5 empty] | 1.644 | 11.017 | 78.934 | 27.386
LIT 225kV N0 2 GIVORS-BANS-GIVORS | 17T000000023677G | RTE | GIVORS-BANS | GIVORS | 220 | 468 | 722 | 722 | 899 | [5 empty] | 0.03 | 0.2 | 0 | 0.5
LIT 225kV N0 2 GIVORS-MIONS | 17T000000024199L | RTE | GIVORS | MIONS | 220 | 576 | 917 | 917 | 1260 | [5 empty] | 0.668 | 6.62 | 75.496 | 20.765
LIT 225kV N0 2 GIVORS-SOLEIL (LE) | 17T000000024200P | RTE | GIVORS | SOLEIL (LE) | 220 | 639 | 717 | 717 | 783 | [5 empty] | 2.802 | 13.691 | 124.388 | 34.932
LIT 225kV N0 2 GRAND-COURONNE-ROUGEMONTIER | 17T000000023727R | RTE | GRAND-COURONNE | ROUGEMONTIER | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 1.43 | 9.58 | 68.702 | 23.822
LIT 225kV N0 2 GRAND-COURONNE-ST ETIENNE DU ROUVRAY | 17T000000023728P | RTE | GRAND-COURONNE | ST ETIENNE DU ROUVRAY | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 0.544 | 3.646 | 26.124 | 9.071
LIT 225kV N0 2 GRAND-COURONNE-VAUPALIERE (LA) | 17T000000023729N | RTE | GRAND-COURONNE | VAUPALIERE (LA) | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 1.53 | 10.18 | 73.2 | 25.444
LIT 225kV N0 2 GRANDE-SYNTHE-WARANDE | 17T000000023815U | RTE | GRANDE-SYNTHE | RANDENS | 220 | 1250 | 1250 | 1250 | 1250 | [5 empty] | 0.884 | 5.893 | 42.554 | 14.713
LIT 225kV N0 2 GRANZAY - ST-FLORENT | 17T000000024378L | RTE | GRANZAY | ST-FLORENT | 220 | 1012 | 1150 | 1150 | 1247 | [5 empty] | 0.645 | 4.296 | 31.062 | 10.767
LIT 225KV N0 2 GRIMAUD - TRANS | 17T000000024461Y | RTE | GRIMAUD | TRANS | 220 | 686 | 686 | 686 | 816 | [5 empty] | 1.682 | 11.13 | 309.878 | 29.772
LIT 225kV N0 2 GROS-CAILLOU - VALENCIENNES | 17T0000000237026 | RTE | GROS-CAILLOU | VALENCIENNES | 220 | 915 | 915 | 1030 | 1075 | [5 empty] | 1.618 | 8.259 | 75.75 | 20.829
LIT 225kV N0 2 GROS-CAILLOU-MASTAING | 17T0000000237042 | RTE | GROS-CAILLOU | MASTAING | 220 | 1273 | 1346 | 1346 | 1453 | [5 empty] | 0.259 | 1.72 | 12.514 | 4.318
LIT 225kV N0 2 HARCOURT (POSTE BLINDE)-RAIE-TORTUE | 17T0000000247688 | RTE | HARCOURT (POSTE BLINDE) | RAIE-TORTUE | 220 | 660 | 660 | 900 | 900 | [5 empty] | 0.218 | 0.842 | 661.654 | 6.253
LIT 225kV N0 2 HAVRE (LE) (POSTE) - PONT-SEPT | 17T000000024775B | RTE | HAVRE (LE) (POSTE) | PONT-SEPT | 220 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.127 | 1.241 | 16.76 | 4.244
LIT 225kV N0 2 HOLQUE-LONGUENESSE | 17T0000000248773 | RTE | HOLQUE | LONGUENESSE | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 0.779 | 5.192 | 37.52 | 12.948
LIT 225kV N0 2 JONQUIERES-ST-CESAIRE | 17T000000025123C | RTE | JONQUIERES | ST-CESAIRE | 220 | 990 | 990 | 1165 | 1165 | [5 empty] | 1.302 | 8.682 | 80.204 | 21.84
LIT 225kV N0 2 LA GAUDIERE - MOREAU | 17T0000000239758 | RTE | GAUDIERE (LA) | MOREAU | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 1.46 | 9.683 | 70.474 | 24.293
LIT 225kV N0 2 LANDERNEAU-MARTYRE (LA) | 17T0000000254214 | RTE | LANDERNEAU | MARTYRE (LA) | 220 | 1056 | 1123 | 1123 | 1189 | [5 empty] | 0.249 | 1.483 | 10.996 | 3.831
LIT 225kV N0 2 LESCAR-MARSILLON | 17T000000025716M | RTE | LESCAR | MARSILLON | 220 | 1172 | 1248 | 1248 | 1310 | [5 empty] | 1.085 | 7.269 | 52.062 | 18.078
LIT 225kV N0 2 LESQUIVE-VERLHAGUET | 17T000000025750M | RTE | LESQUIVE | VERLHAGUET | 220 | 813 | 890 | 890 | 966 | [5 empty] | 2.266 | 10.706 | 71.154 | 25.755
LIT 225kV N0 2 LUMES-MAZURES | 17T0000000260427 | RTE | LUMES | MAZURES | 220 | 843 | 909 | 909 | 996 | [5 empty] | 1.832 | 8.917 | 62.404 | 22.765
LIT 225kV N0 2 LUTTERBACH-SIERENTZ | 17T000000026059R | RTE | LUTTERBACH | SIERENTZ | 220 | 847 | 985 | 985 | 1116 | [5 empty] | 1.375 | 9.208 | 66.028 | 22.9
LIT 225kV N0 2 MALINTRAT-RULHAT | 17T0000000263035 | RTE | MALINTRAT | RULHAT | 220 | 1034 | 1149 | 1149 | 1244 | [5 empty] | 0.357 | 2.344 | 16.41 | 5.787
LIT 225kV N0 2 MAMBELIN-PALENTE | 17T0000000263132 | RTE | MAMBELIN | PALENTE | 220 | 577 | 706 | 706 | 807 | [5 empty] | 3.632 | 21.629 | 147.766 | 52.77
LIT 225kV N0 2 MERLATIERE - SOULLANS | 17T000000026681A | RTE | MERLATIERE | SOULLANS | 220 | 1249 | 1337 | 1337 | 1434 | [5 empty] | 2.6 | 17.383 | 125.114 | 43.412
LIT 225kV N0 2 MEZEROLLES - PORCHEVILLE | 17T0000000267298 | RTE | MEZEROLLES | PORCHEVILLE | 220 | 520 | 782 | 782 | 998 | [5 empty] | 0.371 | 2.447 | 17.698 | 6.134
LIT 225kV N0 2 MIONS - VENISSIEUX | 17T000000026803M | RTE | MIONS | VENISSIEUX | 220 | 1050 | 1050 | 1270 | 1270 | [5 empty] | 0.32 | 2.83 | 94 | 9.493
LIT 225kV N0 2 MIONS-MOUCHE (LA) | 17T000000026802O | RTE | MIONS | MOUCHE (LA) | 220 | 1800 | 1940 | 2030 | 2224 | [5 empty] | 0.44 | 4.31 | 54 | 13.921
LIT 225kV N0 2 MOLE (LA)-RUEYRES | 17T000000026904G | RTE | MOLE (LA) | RUEYRES | 220 | 622 | 748 | 748 | 834 | [5 empty] | 6.805 | 32.206 | 209.352 | 77.606
LIT 225KV N0 2 MONTGROS - PRATCLAUX | 17T000000027185H | RTE | MONTGROS | PRATCLAUX | 220 | 315 | 443 | 443 | 546 | [5 empty] | 3.186 | 9.413 | 127.806 | 22.582
LIT 225kV N0 2 MONTPELLIER - TAMAREAU | 17T000000027228P | RTE | MONTPELLIER | TAMAREAU | 220 | 1161 | 1241 | 1241 | 1306 | [5 empty] | 1.309 | 8.029 | 59.256 | 20.17
LIT 225kV N0 2 MOULINEAUX-VILLEJUST | 17T000000027062X | RTE | MOULINEAUX | VILLEJUST | 220 | 750 | 750 | 1030 | 1030 | [5 empty] | 0.567 | 5.322 | 339.262 | 20.703
LIT 225kV N0 2 PALUN (LA)-SEPTEMES | 17T000000027984O | RTE | PALUN (LA) | SEPTEMES | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 0.911 | 6.115 | 43.724 | 15.6
LIT 225kV N0 2 PESSAC-SAUCATS | 17T000000028125U | RTE | PESSAC | SAUCATS | 220 | 932 | 1049 | 1049 | 1126 | [5 empty] | 1.235 | 8.334 | 63.326 | 21.233
LIT 225kV N0 2 PLAINE HAUTE-TREGUEUX | 17T0000000277455 | RTE | PLAINE HAUTE | TREGUEUX | 220 | 1280 | 1332 | 1332 | 1382 | [5 empty] | 0.837 | 5.591 | 40.242 | 13.946
LIT 225kV N0 2 PLESSIS-GASSOT - VILLIERS-LE-BEL | 17T000000027704J | RTE | PLESSIS-GASSOT | VILLIERS-LE-BEL | 220 | 520 | 782 | 782 | 998 | [5 empty] | 0.191 | 1.278 | 9.19 | 3.259
LIT 225kV N0 2 PLESSIS-GASSOT - PIQUAGE A VILLIERS LE BEL |  | RTE | PLESSIS-GASSOT | PIQUAGE A VILLIERS-LE-BEL | 220 | 948 | 1086 | 1086 | 1211 | [5 empty] | 0.191 | 1.278 | 9.122 | 3.185
LIT 225kV N0 2 PONTEAU - REALTOR | 17T000000028218N | RTE | PONTEAU | REALTOR | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 1.009 | 10.364 | 126.51 | 34.309
LIT 225kV N0 2 PORTET-ST-SIMON - VERFEIL | 17T0000000279059 | RTE | PORTET-ST-SIMON | VERFEIL | 220 | 780 | 780 | 940 | 940 | [5 empty] | 1.773 | 11.735 | 108.132 | 29.255
LIT 225kV N0 2 PRELES (LES)-SEREIN | 17T000000028333N | RTE | PRELES (LES) | SEREIN | 220 | 843 | 909 | 909 | 996 | [5 empty] | 1.266 | 5.727 | 39.918 | 14.135
LIT 225kV N0 2 PRIMEVERES - SAUSSET | 17T000000028339B | RTE | PRIMEVERES | SAUSSET | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 0.467 | 3.125 | 22.442 | 7.79
LIT 225kV N0 2 RAIE-TORTUE-VILLEJUST | 17T000000028487X | RTE | RAIE-TORTUE | VILLEJUST | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 0.453 | 4.383 | 59.988 | 15.219
LIT 225kV N0 2 ROMAINVILLE-VILLEVAUDE | 17T0000000287329 | RTE | ROMAINVILLE | VILLEVAUDE | 220 | 480 | 480 | 835 | 835 | [5 empty] | 1.252 | 6.998 | 347.224 | 19.154
LIT 225kV N0 2 SOLEIL (LE)-VOLVON | 17T000000029044P | RTE | SOLEIL (LE) | VOLVON | 220 | 981 | 1085 | 1085 | 1176 | [5 empty] | 0.891 | 5.957 | 42.864 | 14.858
LIT 225kV N0 2 TAVEL - VIRADEL | 17T0000000293663 | RTE | TAVEL | VIRADEL | 220 | 985 | 985 | 1129 | 1165 | [5 empty] | 2.908 | 18.35 | 197.424 | 46.832
LIT 225kV N0 3 AQUEDUCS (LES) - CIROLLIERS | 17T0000000157883 | RTE | AQUEDUCS (LES) | CIROLLIERS | 220 | 1172 | 1285 | 1285 | 1388 | [5 empty] | 0.552 | 3.677 | 26.592 | 9.219
LIT 225kV N0 3 ARDOISE (L ) - TAVEL | 17T0000000158693 | RTE | ARDOISE (L ) | TAVEL | 220 | 1233 | 1320 | 1320 | 1389 | [5 empty] | 0.648 | 4.319 | 31.088 | 10.612
LIT 225kV N0 3 BEAUTOR (POSTE)-LATENA | 17T000000019065N | RTE | BEAUTOR (POSTE) | LATENA | 220 | 2200 | 2300 | 2300 | 2400 | [5 empty] | 0.944 | 8.865 | 128.308 | 31.467
LIT 225kV N0 3 CAZARIL-LANNEMEZAN | 17T000000019788K | RTE | CAZARIL | LANNEMEZAN | 220 | 1018 | 1117 | 1117 | 1213 | [5 empty] | 0.786 | 4.732 | 34.428 | 11.752
LIT 225kV N0 3 CHAINGY-DAMBRON | 17T000000020071U | RTE | CHAINGY | DAMBRON | 220 | 1099 | 1099 | 1264 | 1264 | [5 empty] | 1.577 | 10.534 | 99.248 | 26.624
LIT 225kV N0 3 CHESNOY (LE)-COURTRY | 17T000000020412U | RTE | CHESNOY (LE) | COURTRY | 220 | 890 | 890 | 1130 | 1130 | [5 empty] | 1.17 | 7.98 | 86 | 20.002
LIT 225kV N0 3 CORBIERE (LA)-DISTRE | 17T000000021144O | RTE | CORBIERE (LA) | DISTRE | 220 | 1249 | 1337 | 1337 | 1434 | [5 empty] | 2.745 | 18.499 | 130.858 | 45.814
LIT 225kV N0 3 GIVORS-BANS-GIVORS | 17T000000023678E | RTE | GIVORS-BANS | GIVORS | 220 | 468 | 722 | 722 | 899 | [5 empty] | 0.03 | 0.23 | 2 | 0.465
LIT 225kV N0 3 GRANDE-SYNTHE-WARANDE | 17T000000023817Q | RTE | GRANDE-SYNTHE | RANDENS | 220 | 1308 | 1408 | 1408 | 1478 | [5 empty] | 0.853 | 5.685 | 41.094 | 14.198
LIT 225kV N0 3 GROS-CAILLOU-MASTAING | 17T000000023707X | RTE | GROS-CAILLOU | MASTAING | 220 | 975 | 1030 | 1030 | 1110 | [5 empty] | 0.497 | 2.478 | 17.502 | 6.105
LIT 225kV N0 3 LUMES - MOHON | 17T0000000260435 | RTE | LUMES | MOHON | 220 | 328 | 554 | 554 | 694 | [5 empty] | 0.357 | 2.325 | 16.86 | 5.5
LIT 225kV N0 3 MEZEROLLES-PORCHEVILLE | 17T000000026730N | RTE | MEZEROLLES | PORCHEVILLE | 220 | 511 | 768 | 768 | 979 | [5 empty] | 0.366 | 2.445 | 17.264 | 6.406
LIT 225kV N0 3 MONTPELLIER - TAMAREAU | 17T000000027229N | RTE | MONTPELLIER | TAMAREAU | 220 | 1200 | 1200 | 1320 | 1389 | [5 empty] | 1.216 | 8.161 | 78.05 | 20.543
LIT 225kV N0 3 ORMES-VESLE | 17T0000000275843 | RTE | ORMES | VESLE | 220 | 1140 | 1248 | 1248 | 1347 | [5 empty] | 1.311 | 8.738 | 61.124 | 21.661
LIT 225kV N0 3 PLESSIS-GASSOT - SEINE | 17T000000027705H | RTE | PLESSIS-GASSOT | SEINE | 220 | 1796 | 1800 | 1975 | 2100 | [5 empty] | 0.491 | 4.808 | 74.298 | 16.391
LIT 225kV N0 3 PORTET-ST-SIMON - VERFEIL | 17T0000000279067 | RTE | PORTET-ST-SIMON | VERFEIL | 220 | 756 | 858 | 858 | 921 | [5 empty] | 2.379 | 12.608 | 86.192 | 30.788
LIT 225kV N0 3 REALTOR - SEPTEMES | 17T0000000285369 | RTE | REALTOR | SEPTEMES | 220 | 1062 | 1160 | 1160 | 1238 | [5 empty] | 0.382 | 2.562 | 24.65 | 7.112
Bosaca - Varin | 24T-V495-0000008 | SEPS | Bosaca | Varin | 400 | [6 empty] | 2000 |  |  | 2.305 | 28.255 | 396.323 | 100.4
Bystricany - Krizovany | 24T-V483-000001Y | SEPS | Bystricany | Krizovany | 400 | [6 empty] | 2000 |  |  | 1.776 | 22.272 | 324.08 | 80
Bystricany - P. Bystrica | 24T-V275-000000D | SEPS | Bystricany | P. Bystrica | 220 | [6 empty] | 665 |  |  | 5.847 | 28.199 | 180.24 | 67
Bystricany - Sucany | 24T-V271-000000C | SEPS | Bystricany | Sucany | 220 | [6 empty] | 665 |  |  | 5.048 | 19.747 | 218.948 | 61.8
Cierny Vah - L. Mara | 24T-V045-000000S | SEPS | Cierny Vah | L. Mara | 400 | [6 empty] | 1200 |  |  | 1.04 | 10.845 | 145.858 | 37.3
Velky Dur - Mochovce | 24T-V048-0000001 | SEPS | Velky Dur | Mochovce | 400 | [6 empty] | 1500 |  |  | 0.162 | 2.063 | 28.651 | 6.9
Velky Dur - Mochovce | 24T-V049-000000T | SEPS | Velky Dur | Mochovce | 400 | [6 empty] | 1500 |  |  | 0.162 | 2.042 | 28.066 | 7.1
J. Bohunice - Bosaca | 24T-V043-0000009 | SEPS | J. Bohunice | Bosaca | 400 | [6 empty] | 1200 |  |  | 0.94 | 11.506 | 165.716 | 41
J. Bohunice - Krizovany | 24T-V044-0000000 | SEPS | J. Bohunice | Krizovany | 400 | [6 empty] | 1200 |  |  | 0.459 | 5.407 | 83.431 | 41
Gabcikovo - P. Biskupice | 24T-V429-0000005 | SEPS | Gabcikovo | P. Biskupice | 400 | [6 empty] | 2280 |  |  | 0.965 | 12.188 | 173.697 | 43
H. Zdana - Sucany | 24T-V493-000000Q | SEPS | H. Zdana | Sucany | 400 | [6 empty] | 2000 |  |  | 1.533 | 19.49 | 275.639 | 69
Kosice - Moldava | 24T-V489-000000J | SEPS | Kosice | Moldava | 400 | [6 empty] | 2355 |  |  | 0.265 | 3.327 | 48.407 | 11.9
Krizovany - P. Biskupice | 24T-V439-000000W | SEPS | Krizovany | P. Biskupice | 400 | [6 empty] | 2010 |  |  | 1.255 | 13.907 | 172.151 | 45.8
Krizovany - Senica | 24T-V283-000000L | SEPS | Krizovany | Senica | 220 | [6 empty] | 785 |  |  | 3.324 | 21.312 | 138.031 | 51.1
Lemesany - Sucany | 24T-V273-000000V | SEPS | Lemesany | Sucany | 220 | [6 empty] | 665 |  |  | 15.389 | 78.86 | 465.282 | 181.2
Lemesany - Vojany | 24T-V071-000000Y | SEPS | Lemesany | Vojany | 220 | [6 empty] | 815 |  |  | 4.984 | 32.974 | 221.49 | 83
Kosice - Lemesany | 24T-V488-000000S | SEPS | Kosice | Lemesany | 400 | [6 empty] | 2000 |  |  | 0.678 | 7.953 | 121.9 | 29.9
Lemesany - Moldava | 24T-V487-0000000 | SEPS | Lemesany | Moldava | 400 | [6 empty] | 2000 |  |  | 0.828 | 9.706 | 148.759 | 41.6
Lemesany - S. Nova Ves | 24T-V408-000000Y | SEPS | Lemesany | S. Nova Ves | 400 | [6 empty] | 1995 |  |  | 1.722 | 17.659 | 222.225 | 58.3
Lemesany - Vola | 24T-V409-000000P | SEPS | Lemesany | Vola | 400 | [6 empty] | 1570 |  |  | 2.308 | 24.226 | 290.504 | 77.8
L. Mara - S. Nova Ves | 24T-V407-0000006 | SEPS | L. Mara | S. Nova Ves | 400 | [6 empty] | 1500 |  |  | 2.536 | 25.758 | 327.994 | 85.7
L. Mara - Varin | 24T-V406-000000F | SEPS | L. Mara | Varin | 400 | [6 empty] | 2000 |  |  | 1.668 | 18.467 | 251.284 | 63.6 | bar: MaximumCurrentImax(A) Period4
L. Mara - Medzibrod | 24T-V461-0000000 | SEPS | L. Mara | Medzibrod | 400 | [6 empty] | 2000 |  |  | 1.222 | 15.129 | 211.348 | 53.2
Moldava - R. Sobota | 24T-V427-000000N | SEPS | Moldava | R. Sobota | 400 | [6 empty] | 2010 |  |  | 2.653 | 28.855 | 350.665 | 93.7
Moldava - V. Kapusany | 24T-V428-000000E | SEPS | Moldava | V. Kapusany | 400 | [6 empty] | 2000 |  |  | 2.583 | 27.946 | 339.12 | 90.3
P. Biskuipice - Stupava | 24T-V498-000000I | SEPS | P. Biskupice | Stupava | 400 | [6 empty] | 2000 |  |  | 1.041 | 12.016 | 191.419 | 45.2
Sucany - Varin | 24T-V405-000000O | SEPS | Sucany | Varin | 400 | [6 empty] | 2000 |  |  | 0.525 | 5.486 | 68.864 | 18.8
Sala - Krizovany | 24T-V279-000000E | SEPS | Sala | Krizovany | 220 | [6 empty] | 785 |  |  | 1.822 | 11.488 | 75.022 | 27.55
Siroka - Sucany | 24T-V281-0000002 | SEPS | Siroka | Sucany | 220 | [6 empty] | 360 |  |  | 2.442 | 14.996 | 105.562 | 37.2
Siroka - Sucany | 24T-V282-000000U | SEPS | Siroka | Sucany | 220 | [6 empty] | 360 |  |  | 2.442 | 14.996 | 105.562 | 37.2
V. Dur - H. Zdana | 24T-V492-000000Z | SEPS | V. Dur | H. Zdana | 400 | [6 empty] | 2000 |  |  | 1.393 | 17.526 | 253.198 | 62.9
V. Dur - Mochovce | 24T-V046-000000J | SEPS | V. Dur | Mochovce | 400 | [6 empty] | 1500 |  |  | 0.153 | 1.956 | 27.161 | 7.1
V. Dur - Levice | 24T-V490-000000G | SEPS | V. Dur | Levice | 400 | [6 empty] | 2000 |  |  | 0.411 | 4.463 | 55.615 | 14.7
V. Dur - Mochovce | 24T-V047-000000A | SEPS | V. Dur | Mochovce | 400 | [6 empty] | 1500 |  |  | 0.156 | 1.985 | 27.562 | 7.2
V. Dur - Krizovany | 24T-V425-0000004 | SEPS | V. Dur | Krizovany | 400 | [6 empty] | 2100 |  |  | 1.809 | 19.632 | 239.032 | 64.1
V. Dur - Levice | 24T-V491-0000007 | SEPS | V. Dur | Levice | 400 | [6 empty] | 2000 |  |  | 0.38 | 4.62 | 71.231 | 17.1
Levice - R. Sobota | 24T-V426-000000W | SEPS | LEVI | R. Sobota | 400 | [6 empty] | 2000 |  |  | 3.339 | 36.258 | 438.496 | 116.3
Medzibrod - Sucany | 24T-V494-000000H | SEPS | Medzibrod | Sucany | 400 | [6 empty] | 2000 |  |  | 1.408 | 17.585 | 245.837 | 62
Vola - V. Kapusany | 24T-V410-000000M | SEPS | Vola | V. Kapusany | 400 | [6 empty] | 1570 |  |  | 1.42 | 15.25 | 191.911 | 50.2
V. Dur - Gabcikovo | 24T-V479-000000T | SEPS | V. Dur | Gabcikovo | 400 | [6 empty] | 2280 |  |  | 2.053 | 25.744 | 374.598 | 92.47
Bosaca - Krizovany | 24T-V496-000001Y | SEPS | Bosaca | Krizovany | 400 | [6 empty] | 2000 |  |  | 1.381 | 15.912 | 265.04 | 60.3
Bystricany - Krizovany | 24T-V484-000000R | SEPS | Bystricany | Krizovany | 400 | [6 empty] | 2000 |  |  | 1.866 | 22.272 | 324.08 | 80
Arad - Nadab | 30TARAD400NADB-P | TEL | Arad | Nadab | 400 | [6 empty] | 1920 |  |  | 1.086 | 9.76 | 131 | 33.6
Bacau Sud - Gutinas | 30TBACS400GUTI-C | TEL | Bacau Sud | Gutinas | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2 | 18.52 | 184 | 55
Bacau Sud - Roman Nord | 30TBACS400ROMN-Q | TEL | Bacau Sud | Roman Nord | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2.06 | 19.44 | 193.001 | 58
Bradu - Brasov | 30TBRAD400BRAS-Y | TEL | Bradu | Brasov | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 5.4 | 50.6 | 500 | 151
Bradu - Tantareni | 30TBRAD400TINT-R | TEL | Bradu | Tantareni | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 7 | 66.5 | 661.001 | 199
Brasov - Darste | 30TBRAS400DIRS-Y | TEL | Brasov | Darste | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 0.46 | 4.39 | 44.001 | 13
Brasov - Sibiu Sud | 30TBRAS400SIBI-1 | TEL | Brasov | Sibiu Sud | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 4.5 | 42.3 | 420.999 | 126
Brazi Vest - Darste | 30TBRAZ400DIRS-1 | TEL | Brazi Vest | Darste | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 4.05 | 38.24 | 380.001 | 114
Bucuresti Sud - Domnesti | 30TBUCU400DOMN-Z | TEL | Bucuresti Sud | Domnesti | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 1.21 | 11.4 | 113.399 | 44
Bucuresti Sud - Gura Ialomitei | 30TBUCU400GIAL-R | TEL | Bucuresti Sud | Gura Ialomitei | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 4.99 | 47.1 | 468.201 | 140
Bucuresti Sud - Pelicanu | 30TBUCU400PELI-W | TEL | Bucuresti Sud | Pelicanu | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 3.83 | 36.25 | 446.301 | 119
Cernavoda - Constanta Nord | 30TCERN400CONS-W | TEL | Cernavoda | Constanta Nord | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2.38 | 22.38 | 251.899 | 73
Cernavoda - Gura Ialomitei c1 | 30TCERN400GIAL1X | TEL | Cernavoda | Gura Ialomitei | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2.26 | 20.8 | 246.1 | 60
Cernavoda - Gura Ialomitei c2 | 30TCERN400GIAL2V | TEL | Cernavoda | Gura Ialomitei | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2.14 | 20.06 | 227.301 | 67
Cernavoda - Pelicanu | 30TCERN400PELI-5 | TEL | Cernavoda | Pelicanu | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 3.23 | 30.2 | 344.9 | 95
Domnesti - Brazi Vest | 30TBRAZ400DOMN-6 | TEL | Domnesti | Brazi Vest | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2.27 | 21.46 | 213 | 64
Domnesti - Urechesti | 30TDOMN400UREC-Q | TEL | Domnesti | Urechesti | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 9.35 | 88.25 | 877.199 | 263
Gadalin - Cluj Est | 30TCLES400GADA-X | TEL | Gadalin | Cluj Est | 400 | [6 empty] | 960 |  |  | 0.69 | 6.5 | 65 | 19
Gura Ialomitei - Lacu Sarat | 30TGIAL400LACS-E | TEL | Gura Ialomitei | Lacu Sarat | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2.38 | 23.7 | 232.999 | 71
Gutinas - Brasov | 30TBRAS400GUTI-F | TEL | Gutinas | Brasov | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 4.4 | 41.3 | 410 | 123
Gutinas - Smardan | 30TGUTI400SMIR-C | TEL | Gutinas | Smardan | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 4.77 | 45.04 | 448.001 | 134
Iernut - Gadalin | 30TGADA400IERN-T | TEL | Iernut | Gadalin | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 1.8 | 16.95 | 168 | 51
Iernut - Sibiu Sud | 30TIERN400SIBI-3 | TEL | Iernut | Sibiu Sud | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2.98 | 28.14 | 280.001 | 84
Isaccea - Lacu Sarat | 30TISAC400LACS-W | TEL | Isaccea | Lacu Sarat | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2.38 | 22.49 | 223.499 | 67
Isaccea - Rahman | 30TISAC400RAHM-V | TEL | Isaccea | Rahman | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 1.66 | 16.89 | 230 | 55.3
Isaccea - Smardan c1 | 30TISAC400SMIR1G | TEL | Isaccea | Smardan | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2 | 18.1 | 197 | 57.1
Isaccea - Smardan c2 | 30TISAC400SMIR2E | TEL | Isaccea | Smardan | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2 | 18.1 | 197 | 56.9
Isaccea - Stupina | 30TISAC400STPA-8 | TEL | Isaccea | Stupina | 400 | [6 empty] | 2000 |  |  | 1.6 | 23.4 | 333 | 82.9
Isaccea - Tulcea Vest | 30TISAC400TULC-7 | TEL | Isaccea | Tulcea Vest | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 1 | 9.57 | 94.999 | 29
Medgidia Sud - Cernavoda | 30TCERN400MEDG-O | TEL | Medgidia Sud | Cernavoda | 400 | [6 empty] | 960 |  |  | 0.71 | 6.23 | 80.5 | 21
Mintia - Arad | 30TARAD400MINT-8 | TEL | Mintia | Arad | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 4.89 | 46.1 | 458.201 | 138
Oradea Sud - Rosiori | 30TORAD400ROSI-1 | TEL | Oradea Sud | Rosiori | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 4.71 | 44.24 | 442 | 133
Portile de Fier - Urechesti | 30TPDFE400UREC-L | TEL | Portile de Fier | Urechesti | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 3.03 | 28.4 | 281.999 | 85
Roman Nord - Suceava | 30TROMN400SUCE-S | TEL | Roman Nord | Suceava | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 3.53 | 33.34 | 331.001 | 99.5
Rosiori - Gadalin | 30TGADA400ROSI-A | TEL | Rosiori | Gadalin | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 4.2 | 39.7 | 394.999 | 119
Sibiu Sud - Mintia | 30TMINT400SIBI-Z | TEL | Sibiu Sud | Mintia | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 4.62 | 43.58 | 432.999 | 130
Sibiu Sud - Tantareni | 30TSIBI400TINT-1 | TEL | Sibiu Sud | Tantareni | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 9.23 | 87.1 | 865.999 | 264
Slatina - Bucuresti Sud | 30TBUCU400SLAT-R | TEL | Slatina | Bucuresti Sud | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 6.14 | 58 | 575.998 | 172
Slatina - Draganesti Olt | 30TDRGO400SLAT-G | TEL | Slatina | Draganesti Olt | 400 | [6 empty] | 960 |  |  | 1.11 | 11.45 | 114.498 | 34
Slatina - Portile de Fier | 30TPDFE400SLAT-S | TEL | Slatina | Portile de Fier | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 5.6 | 52.8 | 526 | 158
Slatina - Tantareni | 30TSLAT400TINTC | TEL | Slatina | Tantareni | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2.98 | 28.14 | 280.001 | 84
Smardan - Lacu Sarat | 30TLACS400SMIR-F | TEL | Smardan | Lacu Sarat | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 1.2 | 11.36 | 113 | 34
Tantareni - Urechesti | 30TTINT400UREC-4 | TEL | Tantareni | Urechesti | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2.5 | 23.3 | 232 | 70
Tariverde - Constanta Nord | 30TCONS400TARV-Y | TEL | Tariverde | Constanta Nord | 400 | MaximumCurrentImax(A) Period1: 1740; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 1.6769 | 15.8627 | 176.399 | 49.5
Tulcea Vest - Tariverde | 30TTARV400TULC1W | TEL | Tulcea Vest | Tariverde | 400 | [6 empty] | 1920 |  |  | 2.3935 | 22.6628 | 288.537 | 74.8
Alba Iulia - Galceag | 30TAIUL220GILC-O | TEL | Alba Iulia | Galceag | 220 | [6 empty] | 600 |  |  | 4.1 | 24.4 | 157.001 | 58
Alba Iulia - Mintia | 30TAIUL220MINT-3 | TEL | Alba Iulia | Mintia | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 6.4 | 35.8 | 229.999 | 84
Alba Iulia - Sugag | 30TAIUL220SUGA-T | TEL | Alba Iulia | Sugag | 220 | [6 empty] | 600 |  |  | 3.34 | 19.74 | 126.999 | 47
Arad - Calea Aradului | 30TARAD220CARA-3 | TEL | Arad | Calea Aradului | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 3.384 | 20 | 128.601 | 48
Arad - Timisoara | 30TARAD220TIMI-5 | TEL | Arad | Timisoara | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 3.8 | 22.6 | 145 | 54
Arefu - Raureni | 30TAREF220RIUR-5 | TEL | Arefu | Raureni | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 3.3 | 19.8 | 126.999 | 81
Baia Mare 3 - Iernut | 30TBAMA220IERN-Y | TEL | Baia Mare 3 | Iernut | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 10.8 | 63.8 | 410 | 152
Baia Mare 3 - Rosiori c1 | 30TBAMA220ROSI1B | TEL | Baia Mare 3 | Rosiori | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 2.35 | 13.91 | 89.419 | 33
Baia Mare 3 - Rosiori c2 | 30TBAMA220ROSI29 | TEL | Baia Mare 3 | Rosiori | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 2.35 | 13.91 | 89.419 | 33
Baia Mare 3 - Tihau | 30TBAMA220TIHA-R | TEL | Baia Mare 3 | Tihau | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 4.1 | 24.2 | 155 | 57
Barbosi - Filesti | 30TBARB220FILE-I | TEL | Barbosi | Filesti | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 0.5 | 2.8 | 18.001 | 7
Baru Mare - Hasdat | 30TBARU220HASD-G | TEL | Baru Mare | Hasdat | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 2.94 | 17.42 | 112.001 | 44
Bradu - Arefu | 30TAREF220BRAD-U | TEL | Bradu | Arefu | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 5.3 | 31.2 | 200 | 74
Bradu - Pitesti Sud | 30TBRAD220PITS-W | TEL | Bradu | Pitesti Sud | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 0.45 | 2.7 | 16.999 | 6
Bradu - Targoviste A | 30TBRAD220TIRG1B | TEL | Bradu | Targoviste A | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 3.8 | 22.5 | 144.001 | 54
Bradu - Targoviste B | 30TBRAD220TIRG29 | TEL | Bradu | Targoviste B | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 3.8 | 22.5 | 144.001 | 54
Brazi Vest - Fundeni c1 | 30TBRAZ220FUND1P | TEL | Brazi Vest | Fundeni | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 4.77 | 28.27 | 181.999 | 67
Brazi Vest - Fundeni c2 | 30TBRAZ220FUND2N | TEL | Brazi Vest | Fundeni | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 4.77 | 28.27 | 181.999 | 67
Brazi Vest - Targoviste A | 30TBRAZ220TIRG1D | TEL | Brazi Vest | Targoviste A | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 3.6 | 21.2 | 136 | 50
Brazi Vest - Targoviste B | 30TBRAZ220TIRG2B | TEL | Brazi Vest | Targoviste B | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 3.6 | 21.2 | 136 | 50
Brazi Vest - Teleajen | 30TBRAZ220TELE-U | TEL | Brazi Vest | Teleajen | 220 | [6 empty] | 720 |  |  | 1.3 | 12.4 | 123 | 32.8
Bucuresti Sud - Ghizdaru d. Mostistea | 30TBUCU220GHMO-E | TEL | Bucuresti Sud | d. Mostistea | 220 | [6 empty] | 561 |  |  | 0.35 | 2.05 | 13 | 4.8
Bucuresti Sud - Fundeni c1 | 30TBUCU220FUND1H | TEL | Bucuresti Sud | Fundeni | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 1.8 | 10.5 | 67.579 | 25
Bucuresti Sud - Fundeni c2 | 30TBUCU220FUND2F | TEL | Bucuresti Sud | Fundeni | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 1.8 | 10.5 | 67.579 | 25
Bucuresti Sud - Ghizdaru | 30TBUCU220GHIZ-Y | TEL | Bucuresti Sud | Ghizdaru | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 5.14 | 30.4 | 196.001 | 72
Calea Aradului - Sacalaz | 30TCARA220SACA-P | TEL | Calea Aradului | Sacalaz | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 0.553 | 3.269 | 21.022 | 47.63
Campia Turzii - Iernut | 30TCTRZ220IERN-6 | TEL | Campia Turzii | Iernut | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 4.8 | 26.9 | 173.001 | 51
Cetate - Calafat | 30TCALF220CETA-C | TEL | Cetate | Calafat | 220 | [6 empty] | 720 |  |  | 2.5 | 14.78 | 95.13 | 36
Cetate - Portile de Fier c1 | 30TCETA220PDFE14 | TEL | Cetate | Portile de Fier | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 6.56 | 38.84 | 250 | 92
Cetate - Portile de Fier c2 | 30TCETA220PDFE22 | TEL | Cetate | Portile de Fier | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 6.56 | 38.84 | 249.999 | 92
Cluj Floresti - Alba Iulia | 30TAIUL220CJFL-3 | TEL | Cluj Floresti | Alba Iulia | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 7.2 | 40.4 | 260.001 | 96
Cluj Floresti - Campia Turzii | 30TCJFL220CTRZ-R | TEL | Cluj Floresti | Campia Turzii | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 1.98 | 11.76 | 142.999 | 41
Cluj Floresti - Mariselu | 30TCJFL220MARI-2 | TEL | Cluj Floresti | Mariselu | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 1.8 | 10.7 | 68.999 | 25
Craiova Nord - Isalnita c1 | 30TCRAI220ISAL1H | TEL | Craiova Nord | Isalnita | 220 | [6 empty] | 1185 |  |  | 0.57 | 3.709 | 15 | 10
Craiova Nord - Isalnita c2 | 30TCRAI220ISAL2F | TEL | Craiova Nord | Isalnita | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 0.68 | 3.84 | 26 | 10
Craiova Nord - Sardanesti | 30TCRAI220SARD-7 | TEL | Craiova Nord | Sardanesti | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 5.4 | 29.35 | 187.999 | 68.6
Craiova Nord - Slatina | 30TCRAI220SLAT-9 | TEL | Craiova Nord | Slatina | 220 | MaximumCurrentImax(A) Period1: 1600; MaximumCurrentImax(A) Period2: 1780; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2 | 10.32 | 265.999 | 49
FAI - Gutinas | 30TGUTI220IASI-A | TEL | FAI | Gutinas | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 13.5 | 79.8 | 513 | 190
FAI - Munteni | 30TIASI220MUNV-I | TEL | FAI | Munteni | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 5.28 | 31.2 | 200 | 74
FAI - Suceava | 30TIASI220SUCE-3 | TEL | FAI | Suceava | 220 | [6 empty] | 720 |  |  | 8.23 | 48.75 | 313 | 116
Fantanele - Gheorgheni | 30TFINT220GHEO-R | TEL | Fantanele | Gheorgheni | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 6.2 | 32.7 | 210 | 78
Filesti - Lacu Sarat | 30TFILE220LACS-F | TEL | Filesti | Lacu Sarat | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 2.1 | 12.2 | 77.999 | 29
Focsani Vest - Barbosi | 30TBARB220FCSV-6 | TEL | Focsani Vest | Barbosi | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 5.81 | 30.49 | 204.91 | 90
Gheorgheni - Stejaru | 30TGHEO220STEJ-L | TEL | Gheorgheni | Stejaru | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 960 |  |  |  | 5.3 | 27.9 | 180.001 | 59.5
Ghizdaru - Turnu Magurele | 30TGHIZ220TMAG-W | TEL | Ghizdaru | Turnu Magurele | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 5.83 | 34.54 | 222.001 | 82
Gradiste - Isalnita | 30TGRAD220ISAL-J | TEL | Gradiste | Isalnita | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 2.564 | 15.167 | 290.99 | 60
Gutinas - Dumbrava | 30TDUMB220GUTI-U | TEL | Gutinas | Dumbrava | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 6.43 | 38.1 | 245 | 81
Gutinas - Focsani Vest | 30TFCSV220GUTI-S | TEL | Gutinas | Focsani Vest | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 5.552 | 29.15 | 196.14 | 86
Gutinas - Munteni | 30TGUTI220MUNV-F | TEL | Gutinas | Munteni | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 8.3 | 49.1 | 316 | 116
Hasdat - Mintia | 30THASD220MINT1W | TEL | Hasdat | Mintia | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 1.83 | 10.82 | 70.001 | 26
Hasdat - Otelarie H | 30THASD220HDOT-D | TEL | Hasdat | Otelarie H | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 0.53 | 3.12 | 19.999 | 7
Hasdat - Pestis | 30THASD220PEST-I | TEL | Hasdat | Pestis | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 1.3 | 7 | 45 | 16
Iaz - Resita c1 | 30TIAZU220RESI1Y | TEL | Iaz | Resita | 220 | [6 empty] | 720 |  |  | 2.18 | 12.91 | 80.001 | 31
Iaz - Resita c2 | 30TIAZU220RESI2W | TEL | Iaz | Resita | 220 | [6 empty] | 720 |  |  | 2.18 | 12.91 | 80.001 | 31
Iernut - Ungheni c1 | 30TIERN220UNGH1L | TEL | Iernut | Ungheni | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 2.28 | 12.31 | 78.998 | 29
Iernut - Ungheni c2 | 30TIERN220UNGH2J | TEL | Iernut | Ungheni | 220 | [6 empty] | 1200 |  |  | 1.13 | 10 | 97 | 29
Lotru - Sibiu Sud c1 | 30TLOTR220SIBI12 | TEL | Lotru | Sibiu Sud | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 6.25 | 36.96 | 236.999 | 85
Lotru - Sibiu Sud c2 | 30TLOTR220SIBI20 | TEL | Lotru | Sibiu Sud | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 6.25 | 36.96 | 236.999 | 85
Mintia - Pestis c1 | 30TMINT220PEST17 | TEL | Mintia | Pestis | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 1.33 | 7.84 | 49.998 | 19
Mintia - Pestis c2 | 30TMINT220PEST2 | TEL | Mintia | Pestis | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 1.33 | 7.84 | 49.998 | 19
Mintia - Timisoara | 30TMINT220TIMI-O | TEL | Mintia | Timisoara | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 9.2 | 54.7 | 352 | 130
Paroseni - Baru Mare | 30TBARU220PARO-D | TEL | Paroseni | Baru Mare | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 1.6 | 8.5 | 55 | 20
Paroseni - Targiu Jiu Nord | 30TPARO220TRGJ-Q | TEL | Paroseni | Targiu Jiu Nord | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 3 | 15.83 | 102.001 | 38
Pestis - Otelarie H | 30THDOT220PEST-E | TEL | Pestis | Otelarie H | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 0.83 | 4.73 | 30.429 | 11
Portile de Fier - Resita c1 | 30TPDFE220RESI1S | TEL | Portile de Fier | Resita | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 8.3 | 49.14 | 316 | 117
Portile de Fier - Resita c2 | 30TPDFE220RESI2Q | TEL | Portile de Fier | Resita | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 8.3 | 49.14 | 316 | 117
Portile de Fier - Turnu Severin Est c1 | 30TDROB220PDFE1S | TEL | Portile de Fier | Turnu Severin Est | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 0.92 | 5.45 | 35 | 13
Portile de Fier - Turnu Severin Est c2 | 30TDROB220PDFE2Q | TEL | Portile de Fier | Turnu Severin Est | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 0.92 | 5.45 | 35 | 13
Raureni - Stuparei | 30TRIUR220STUP-M | TEL | Raureni | Stuparei | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 0.9 | 5.1 | 32.999 | 12
Resita - Timisoara c1 | 30TRESI220TIMI1L | TEL | Resita | Timisoara | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 5.2 | 30.7 | 197 | 73
Resita - Timisoara c2 | 30TRESI220TIMI2J | TEL | Resita | Timisoara | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 5.2 | 30.7 | 197 | 73
Retezat - Hasdat | 30THASD220RETE-A | TEL | Retezat | Hasdat | 220 | [6 empty] | 1200 |  |  | 0.98 | 13.8 | 136.999 | 41
Rosiori - Vetis | 30TROSI220VETI--R | TEL | Rosiori | Vetis | 220 | [6 empty] | 720 |  |  | 2.45 | 14.7 | 94.499 | 35
Sacalaz - Timisoara | 30TSACA220TIMI-K | TEL | Sacalaz | Timisoara | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 1.7 | 10.3 | 65.999 | 25
Sardanesti - Urechesti | 30TSARD220UREC-9 | TEL | Sardanesti | Urechesti | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 5.14 | 28.34 | 181.999 | 65.9
Slatina - Gradiste | 30TGRAD220SLAT-7 | TEL | Slatina | Gradiste | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 1.263 | 7.47 | 93.051 | 23.3
Stalpu - Teleajen | 30TTLP220TELEAJC | TEL | Stalpu | Teleajen | 220 | [6 empty] | 960 |  |  | 1.9 | 17.9 | 177.999 | 53
Stejaru - Dumbrava | 30TDUMB220STEJ-K | TEL | Stejaru | Dumbrava | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 2.4 | 14.2 | 90.999 | 34
Stuparei - Bradu | 30TBRAD220STUP-1 | TEL | Stuparei | Bradu | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 5 | 29.7 | 190.999 | 71
Tihau - Cluj Floresti | 30TCJFL220TIHA-L | TEL | Tihau | Cluj Floresti | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 4.7 | 28 | 180.001 | 67
Tihau - Salaj | 30TSALJ220TIHA-N | TEL | Tihau | Salaj | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 960; MaximumCurrentImax(A) Period3: 960 |  |  |  | 1.92 | 11.34 | 73.001 | 27
Turnu Magurele - Craiova Nord | 30TCRAI220TMAG-0 | TEL | Turnu Magurele | Craiova Nord | 220 | MaximumCurrentImax(A) Period1: 870; MaximumCurrentImax(A) Period2: 970; MaximumCurrentImax(A) Period3: 1062 |  |  |  | 8.55 | 50.6 | 325.001 | 120
Ungheni - Fantanele | 30TFINT220UNGH-0 | TEL | Ungheni | Fantanele | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 2 | 11.3 | 73.001 | 26
Urechesti - Targu Jiu Nord | 30TTRGJ220UREC-1 | TEL | Urechesti | Targu Jiu Nord | 220 | MaximumCurrentImax(A) Period1: 800; MaximumCurrentImax(A) Period2: 890; MaximumCurrentImax(A) Period3: 978 |  |  |  | 1.35 | 7.57 | 48.999 | 18
Nadab - Oradea Sud | 30TORAD400NADAB7 | TEL | Nadab | Oradea Sud | 400 | MaximumCurrentImax(A) Period1: 1920; MaximumCurrentImax(A) Period2: 1920; MaximumCurrentImax(A) Period3: 1920 |  |  |  | 2.348 | 21.059 | 283.8999 | 33.6
Beverwijk-Oostzaan 380 W | 49T0000000000517 | TENNET NL | Oostzaan | Beverwijk | 400 | MaximumCurrentImax(A) Period1: 2890; MaximumCurrentImax(A) Period2: 3300 |  |  |  | 0.3717 | 4.3527 | 65.4243 | 17
Beverwijk-Oostzaan 380 Z | 49T0000000000509 | TENNET NL | Oostzaan | Beverwijk | 400 | MaximumCurrentImax(A) Period1: 2890; MaximumCurrentImax(A) Period2: 3300 |  |  |  | 0.3717 | 4.3527 | 65.4243 | 17
Beverwijk-Vijfhuizen 380 W | 49T000000000049V | TENNET NL | Beverwijk | Vijfhuizen | 400 | MaximumCurrentImax(A) Period1: 3000; MaximumCurrentImax(A) Period2: 3000 |  |  |  | 0.3667 | 2.8601 | 164.002 | 14.31
Beverwijk-Vijfhuizen 380 Z | 49T000000000048X | TENNET NL | Beverwijk | Vijfhuizen | 400 | MaximumCurrentImax(A) Period1: 3000; MaximumCurrentImax(A) Period2: 3000 |  |  |  | 0.3667 | 2.8601 | 164.002 | 14.31
Bleiswijk-Vijfhuizen 380 O | 49T000000000047Z | TENNET NL | Bleiswijk | Vijfhuizen | 400 | MaximumCurrentImax(A) Period1: 3000; MaximumCurrentImax(A) Period2: 3000 |  |  |  | 1.0709 | 10.191 | 1425.929 | 45.944
Bleiswijk-Vijfhuizen 380 P | 49T0000000000460 | TENNET NL | Bleiswijk | Vijfhuizen | 400 | MaximumCurrentImax(A) Period1: 3000; MaximumCurrentImax(A) Period2: 3000 |  |  |  | 1.0709 | 10.191 | 1425.929 | 45.944
Borssele-Rilland 380 G | 49T000000000057W | TENNET NL | Borssele | Rilland | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3300 |  | 2500 | 4000 | 0.8696 | 10.184 | 153.0682 | 38.924
Borssele-Rilland 380 Z | 49T000000000059S | TENNET NL | Borssele | Rilland | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3300 |  | 2500 | 4000 | 0.8696 | 10.184 | 153.0682 | 38.924
Boxmeer-Dodewaard 380 Z | 49T000000000006C | TENNET NL | Dodewaard | Boxmeer | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2875 |  |  |  | 0.9702 | 11.421 | 171.589 | 41.7
Breukelen Kortrijk-Diemen 380 W | 49T0000000000088 | TENNET NL | Breukelen Kortrijk | Diemen | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 0.4402 | 5.1553 | 134.2988 | 37.52
Crayestein-Krimpen a/d IJssel 380 W | 49T0000000000347 | TENNET NL | Crayestein | Krimpen a/d IJssel | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.2266 | 3.5957 | 71.6983 | 14.835
Crayestein-Krimpen a/d IJssel 380 Z | 49T0000000000339 | TENNET NL | Crayestein | Krimpen a/d IJssel | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.2266 | 3.5957 | 71.6983 | 14.835
Diemen-Lelystad 380 W | 49T0000000000096 | TENNET NL | Diemen | Lelystad | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 1.1803 | 13.714 | 209.651 | 50.43
Diemen-Lelystad 380 Z | 49T000000000010L | TENNET NL | Diemen | Lelystad | 400 | MaximumCurrentImax(A) Period1: 2800; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 1.1803 | 13.714 | 209.651 | 50.43
Dodewaard-Doetinchem 380 W | 49T000000000011J | TENNET NL | Dodewaard | Doetinchem | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 1.1555 | 12.372 | 192.8592 | 45.4
Dodewaard-Doetinchem 380 Z | 49T000000000012H | TENNET NL | Dodewaard | Doetinchem | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 1.1555 | 12.372 | 192.8592 | 45.4
Doetinchem-Hengelo 380 W | 49T000000000014D | TENNET NL | Doetinchem | Hengelo | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 1.491 | 16.04 | 247.7843 | 58.65
Doetinchem-Hengelo 380 Z | 49T000000000015B | TENNET NL | Doetinchem | Hengelo | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 1.491 | 16.04 | 247.7843 | 58.65
Eemshaven - Eemshaven het Hogeland 380 Zwart | 49T000000000105A | TENNET NL | Eemshaven | Eemshaven het Hogeland | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.0064 | 0.1329 | 58.8558 | 0.8
Eemshaven het Hogeland - Meeden 380 Zwart | 49T0000000001068 | TENNET NL | Eemshaven het Hogeland | Meeden | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.5196 | 8.8231 | 182.3658 | 37.2
Eemshaven Oude Schip -Eemshaven 380 W | 49T0000000000177 | TENNET NL | Eemshaven | Eemshaven Oude Schip | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.0213 | 0.3341 | 6.9216 | 1.44
Eemshaven Oude Schip -Eemshaven 380 Z | 49T0000000000185 | TENNET NL | Eemshaven | Eemshaven Oude Schip | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.0213 | 0.3341 | 6.9216 | 1.44
Eemshaven Oude Schip-Doekegat 380 W | 49T0000000000541 | TENNET NL | Eemshaven Oude Schip | Doekegat | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.0244 | 0.275 | 4.1469 | 1
Eemshaven Oude Schip-Doekegat 380 Z | 49T0000000000533 | TENNET NL | Eemshaven Oude Schip | Doekegat | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.0244 | 0.275 | 4.1469 | 1
Eemshaven-Meeden 380 W | 49T000000000004G | TENNET NL | Eemshaven | Meeden | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.5196 | 8.8231 | 182.3658 | 36.8
Ens-Zwolle 380 W | 49T000000000024A | TENNET NL | Ens | Zwolle | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 0.81 | 8.7474 | 135.3747 | 32
Ens-Zwolle 380 Z | 49T0000000000258 | TENNET NL | Ens | Zwolle | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 0.81 | 8.7474 | 135.3747 | 32
Geertruidenberg-Eindhoven 380 G | 49T0000000000193 | TENNET NL | Geertruidenberg | Eindhoven | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 1.47 | 19.026 | 244.9655 | 63.9
Geertruidenberg-Eindhoven 380 W | 49T000000000020I | TENNET NL | Geertruidenberg | Eindhoven | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 1.4985 | 19.03 | 244.3273 | 63.9
Geertruidenberg-Eindhoven 380 Z | 49T000000000021G | TENNET NL | Geertruidenberg | Eindhoven | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 1.5064 | 19.131 | 245.6273 | 63.9
Krimpen a/d IJssel-Bleiswijk 380 W | 49T0000000000452 | TENNET NL | Krimpen a/d IJssel | Bleiswijk | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.2831 | 4.5209 | 88.9798 | 18.56
Krimpen a/d IJssel-Bleiswijk 380 Z | 49T0000000000444 | TENNET NL | Krimpen a/d IJssel | Bleiswijk | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.2831 | 4.5209 | 88.9798 | 18.56
Krimpen a/d IJssel-Breukelen Kortrijk 380 W | 49T0000000000266 | TENNET NL | Krimpen a/d IJssel | Breukelen Kortrijk | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 0.9046 | 10.593 | 275.9644 | 20.01
Krimpen a/d IJssel-Geertruidenberg 380 W | 49T0000000000274 | TENNET NL | Krimpen a/d IJssel | Geertruidenberg | 400 | MaximumCurrentImax(A) Period1: 2826; MaximumCurrentImax(A) Period2: 3300 |  |  |  | 0.7952 | 9.313 | 139.9833 | 34.02
Krimpen a/d IJssel-Geertruidenberg 380 Z | 49T0000000000282 | TENNET NL | Krimpen a/d IJssel | Geertruidenberg | 400 | MaximumCurrentImax(A) Period1: 2826; MaximumCurrentImax(A) Period2: 3300 |  |  |  | 0.7952 | 9.313 | 139.9833 | 34.02
Krimpen a/d IJssel-Oostzaan 380 Z | 49T000000000032B | TENNET NL | Krimpen a/d IJssel | Oostzaan | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 1.7021 | 19.909 | 299.2586 | 72.529
Lelystad-Ens 380 W | 49T000000000022E | TENNET NL | Lelystad | Ens | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.4921 | 5.7228 | 86.9979 | 21
Lelystad-Ens 380 Z | 49T000000000023C | TENNET NL | Lelystad | Ens | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.4921 | 5.7228 | 86.9979 | 21
Maasbracht-Boxmeer 380 Z | 49T000000000007A | TENNET NL | Maasbracht | Boxmeer | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2875 |  |  |  | 1.3472 | 15.858 | 238.2494 | 57.9
Maasbracht-Dodewaard 380 W | 49T000000000013F | TENNET NL | Maasbracht | Dodewaard | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 2.3161 | 27.281 | 409.8279 | 99.6
Maasbracht-Eindhoven 380 W | 49T0000000000290 | TENNET NL | Maasbracht | Eindhoven | 400 | MaximumCurrentImax(A) Period1: 2826; MaximumCurrentImax(A) Period2: 3300 |  |  |  | 1.1334 | 13.351 | 200.5604 | 48.742
Maasbracht-Eindhoven 380 Z | 49T000000000030F | TENNET NL | Maasbracht | Eindhoven | 400 | MaximumCurrentImax(A) Period1: 2826; MaximumCurrentImax(A) Period2: 3300 |  |  |  | 1.1334 | 13.351 | 200.5604 | 48.742
Maasvlakte-Simonshaven 380 W | 49T0000000000371 | TENNET NL | Maasvlakte | Simonshaven | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.3972 | 6.3019 | 125.6594 | 26
Maasvlakte-Simonshaven 380 Z | 49T000000000039Y | TENNET NL | Maasvlakte | Simonshaven | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.3972 | 6.3019 | 125.6594 | 26
Oostzaan-Diemen 380 G | 49T0000000000525 | TENNET NL | Oostzaan | Diemen | 400 | MaximumCurrentImax(A) Period1: 2890; MaximumCurrentImax(A) Period2: 3000 |  |  |  | 0.3553 | 4.161 | 62.544 | 15.2
Rilland-Geertruidenberg 380 W | 49T000000000058U | TENNET NL | Rilland | Geertruidenberg | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 1.5733 | 17.255 | 259.0317 | 61.213
Rilland-Geertruidenberg 380 Z | 49T0000000000606 | TENNET NL | Rilland | Geertruidenberg | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 1.5733 | 17.255 | 259.0317 | 61.213
Simonshaven-Crayestein 380 W | 49T0000000000355 | TENNET NL | Simonshaven | Crayestein | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.6176 | 9.7995 | 195.4003 | 40.43
Simonshaven-Crayestein 380 Z | 49T0000000000363 | TENNET NL | Simonshaven | Crayestein | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.6176 | 9.7995 | 195.4003 | 40.43
Wateringen-Bleiswijk 380 W | 49T0000000000428 | TENNET NL | Wateringen | Bleiswijk | 400 | MaximumCurrentImax(A) Period1: 2470; MaximumCurrentImax(A) Period2: 2470 |  |  |  | 0.176 | 3.6546 | 1618.536 | 22
Wateringen-Bleiswijk 380 Z | 49T0000000000436 | TENNET NL | Wateringen | Bleiswijk | 400 | MaximumCurrentImax(A) Period1: 2470; MaximumCurrentImax(A) Period2: 2470 |  |  |  | 0.176 | 3.6546 | 1618.536 | 22
Wateringen-Westerlee 380 W | 49T000000000041A | TENNET NL | Wateringen | Westerlee | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.1034 | 1.6621 | 32.4898 | 6.8
Wateringen-Westerlee 380 Z | 49T000000000040C | TENNET NL | Wateringen | Westerlee | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.1034 | 1.6621 | 32.4898 | 6.8
Westerlee-Maasvlakte 380 W | 49T000000000069P | TENNET NL | Maasvlakte | Westerlee | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.284 | 12.0269 | 224.01 | 20.432
Westerlee-Maasvlakte 380 Z | 49T0000000000703 | TENNET NL | Maasvlakte | Westerlee | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.284 | 12.0269 | 224.01 | 20.432
Zwolle-Hengelo 380 W | 49T000000000000O | TENNET NL | Zwolle | Hengelo | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 1.5301 | 16.526 | 253.9931 | 60.31
Zwolle-Hengelo 380 Z | 49T000000000031D | TENNET NL | Zwolle | Hengelo | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 1.5301 | 16.526 | 253.9931 | 60.31
Zwolle-Meeden 380 W | 49T000000000001M | TENNET NL | Zwolle | Meeden | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 1.4968 | 25.632 | 522.3601 | 107.85
Zwolle-Meeden 380 Z | 49T000000000002K | TENNET NL | Zwolle | Meeden | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 1.5013 | 25.634 | 522.3352 | 107.85
Eemshaven-Eemshaven Oost 220 W | 49T000000000193O | TENNET NL | Eemshaven | Eemshaven Oost | 220 | MaximumCurrentImax(A) Period1: 600; MaximumCurrentImax(A) Period2: 600 |  |  |  | 0.075 | 0.104 | 135.0401 | 0.93
Eemshaven-Eemshaven Oost 220 Z | 49T000000000194M | TENNET NL | Eemshaven | Eemshaven Oost | 220 | MaximumCurrentImax(A) Period1: 600; MaximumCurrentImax(A) Period2: 600 |  |  |  | 0.075 | 0.104 | 135.0401 | 0.93
Eemshaven-Robbenplaat 220 A | 49T000000000195K | TENNET NL | Eemshaven | Robbenplaat | 220 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.0043 | 0.0501 | 9.2235 | 0.04
Eemshaven-Robbenplaat 220 B | 49T000000000196I | TENNET NL | Eemshaven | Robbenplaat | 220 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.0043 | 0.0501 | 9.2235 | 0.04
Hessenweg-Ens 220 W | 49T000000000197G | TENNET NL | Hessenweg | Ens | 220 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 0.7489 | 8.2606 | 138.1198 | 31.4101
Hessenweg-Ens 220 Z | 49T000000000198E | TENNET NL | Hessenweg | Ens | 220 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 0.7489 | 8.2606 | 138.1198 | 31.4101
Hessenweg-Zeyerveen 220 W | 49T000000000199C | TENNET NL | Hessenweg | Zeyerveen | 220 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2750 |  |  |  | 1.302 | 18.72 | 230.906 | 64.052
Hessenweg-Zeyerveen 220 Z | 49T000000000200G | TENNET NL | Hessenweg | Zeyerveen | 220 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2750 |  |  |  | 1.302 | 18.72 | 230.906 | 64.052
Louwsmeer-Bergum 220 W | 49T0000000000614 | TENNET NL | Louwsmeer | Bergum | 220 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 0.2592 | 2.8519 | 47.6976 | 10.847
Louwsmeer-Bergum 220 Z | 49T0000000000622 | TENNET NL | Louwsmeer | Bergum | 220 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 0.2594 | 2.8517 | 47.6992 | 10.847
Louwsmeer-Oudehaske 220 W | 49T000000000064Z | TENNET NL | Louwsmeer | Oudehaske | 220 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2750 |  |  |  | 0.6808 | 7.4894 | 125.2591 | 28.4854
Louwsmeer-Oudehaske 220 Z | 49T000000000065X | TENNET NL | Louwsmeer | Oudehaske | 220 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2750 |  |  |  | 0.6813 | 7.4889 | 125.2633 | 28.4854
Meeden-Weiwerd 220 B | 49T000000000201E | TENNET NL | Meeden | Weiwerd | 220 | MaximumCurrentImax(A) Period1: 2300; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 0.4921 | 7.2484 | 139.7185 | 29.6
Meeden-Weiwerd 220 O | 49T000000000202C | TENNET NL | Meeden | Weiwerd | 220 | MaximumCurrentImax(A) Period1: 2300; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 0.4924 | 7.208 | 140.388 | 29.6
Oudehaske-Ens 220 W | 49T000000000066V | TENNET NL | Oudehaske | Ens | 220 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 1.0467 | 11.515 | 192.5915 | 43.7976
Oudehaske-Ens 220 Z | 49T000000000067T | TENNET NL | Oudehaske | Ens | 220 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2750 |  |  |  | 1.0467 | 11.515 | 192.5915 | 43.7976
Robbenplaat-Weiwerd 220 P | 49T000000000203A | TENNET NL | Robbenplaat | Weiwerd | 220 | MaximumCurrentImax(A) Period1: 2300; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 0.4164 | 5.9349 | 112.1255 | 25.6
Robbenplaat-Eemshaven het Hogeland 220 G | 49T0000000002129 | TENNET NL | Robbenplaat | Eemshaven het Hogeland | 220 | MaximumCurrentImax(A) Period1: 2300; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 0.0108 | 0.1834 | 0 | 0.8
Eemshaven het Hogeland-Weiwerd 220G | 49T0000000002161 | TENNET NL | Eemshaven het Hogeland | Weiwerd | 220 | MaximumCurrentImax(A) Period1: 2300; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 0.4037 | 5.7814 | 0 | 23.2
Vierverlaten-Eemshaven 220 G | 49T0000000000630 | TENNET NL | Vierverlaten | Eemshaven | 220 | MaximumCurrentImax(A) Period1: 2300; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 0.9897 | 11.441 | 160.4802 | 40.02
Vierverlaten-Robbenplaat 220 W | 49T0000000002153 | TENNET NL | Vierverlaten | Robbenplaat | 220 | MaximumCurrentImax(A) Period1: 2300; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 1.009 | 11.195 | 0 | 39.93
Vierverlaten-Zeyerveen 220 W | 49T0000000002064 | TENNET NL | Vierverlaten | Zeyerveen | 220 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2750 |  |  |  | 0.4 | 6.97 | 90.84 | 22.71
Vierverlaten-Zeyerveen 220 Z | 49T0000000002072 | TENNET NL | Vierverlaten | Zeyerveen | 220 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2750 |  |  |  | 0.4 | 6.97 | 90.84 | 22.71
Bergum-Vierverlaten 220 W | 49T000000000068R | TENNET NL | Bergum | Vierverlaten | 220 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 0.726 | 8.2764 | 153.3047 | 32.4798
Bergum - Robbenplaat 220 Z | 49T0000000001076 | TENNET NL | Bergum | Robbenplaat | 220 | MaximumCurrentImax(A) Period1: 2300; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 1.7131 | 19.691 | 313.8233 | 72.41
Altheim - Sittling 219 | 11TD2L000000003L | TENNETGMBH | Altheim | Sittling | 220 | [7 empty] | 834 | 1274.49 | 4.07 | 18.26 | 129.1195 | 45.6164
Y-Simbach (-Altheim - St. Peter) 233/230 | 11T0-0000-0984-D | TENNETGMBH | Altheim | Y-Simbach | 220 | [7 empty] | 834 | 1200 | 5.649 | 27.976 | 201.577 | 70.705
Altheim - Sittling 220 | 11TD2L000000004J | TENNETGMBH | Altheim | Sittling | 220 | [7 empty] | 834 | 1274 | 4.07 | 18.26 | 129.12 | 45.58
Y-Simbach (-Altheim - St. Peter) 234/230 | 11T0-0000-0986-7 | TENNETGMBH | Altheim | Y-Simbach | 220 | [7 empty] | 834 | 1200 | 5.6488 | 27.983 | 201.5332 | 70.2957
Y-Alfstedt (-Alfstedt - Farge - Dollern) blau | 11T0-0000-1069-8 | TENNETGMBH | Alfstedt | Y-Alfstedt | 400 | [6 empty] | 600 |  |  | 0.003 | 0.1 | 0.383 | 0.02
Y-Alfstedt (-Alfstedt - Elsfleth/W - Dollern) schwarz | 11T0-0000-1113-4 | TENNETGMBH | Alfstedt | Y-Alfstedt | 400 | [6 empty] | 600 |  |  | 0.001 | 0.1 | 0.075 | 0.02
Wahle - Algermissen 2 | 11TD2L000000238V | TENNETGMBH | Algermissen | Wahle | 400 | [7 empty] | 2720 | 3150 | 0.9 | 8.167 | 145.896 | 33.423
Aschaffenburg - Bergrheinfeld/W 418 | 11T0-0000-0044-0 | TENNETGMBH | Aschaffenburg | Bergrheinfeld/W | 400 | [6 empty] | 2616 |  |  | 2.141 | 22.444 | 352.019 | 83.613
Audorf - Audorf/S 421 | 11TD2L0000000099 | TENNETGMBH | Audorf | Audorf | 220 | [6 empty] | 1441 |  |  | 0 | 0.1 | 0.031 | 0.35
Audorf/S - Kummerfeld schwarz | 11T0-0000-0039-Q | TENNETGMBH | Audorf/S | Kummerfeld | 400 | [6 empty] | 3600 |  |  | 1.131 | 20.42 | 404.637 | 85.428
Wilster/W - Audorf/S blau | 11TD2L000000249Q | TENNETGMBH | Audorf/S | Wilster/W | 400 | [6 empty] | 2216 |  |  | 1.318 | 15.41 | 194.779 | 50.874
Wilster/W - Audorf/S rot | 11TD2L0000002504 | TENNETGMBH | Audorf/S | Wilster/W | 400 | [6 empty] | 2216 |  |  | 1.318 | 15.41 | 194.779 | 50.852
Audorf/S - Handewitt gruen | 11T0-0000-1516-C | TENNETGMBH | Audorf/S | Handewitt | 400 | [6 empty] | 2216 |  |  | 1.7369 | 19.862 | 256.2346 | 67.0545
Bechterdissen - Eickum 1 | 11TD2L0000000625 | TENNETGMBH | Bechterdissen | Eickum | 400 | [6 empty] | 3150 |  |  | 0.412 | 3.749 | 66.564 | 14.939
Bechterdissen - Eickum 3 | 11T0-0000-1548-V | TENNETGMBH | Bechterdissen | Eickum | 400 | [6 empty] | 3126 |  |  | 0.412 | 3.749 | 66.564 | 15.105
Bechterdissen - Veltheim A01 | 11TD2L000000356P | TENNETGMBH | Bechterdissen | Veltheim | 220 | [7 empty] | 918 | 1310 | 1.965 | 9.941 | 133.8 | 34.222
Bechterdissen - Lage A03 | 11TD2L0000003055 | TENNETGMBH | Bechterdissen | Lage | 220 | [6 empty] | 1310 |  |  | 0.637 | 3.764 | 43.825 | 12.031
Veltheim - Bechterdissen A07 | 11TD2L0000003411 | TENNETGMBH | Bechterdissen | Veltheim | 220 | [7 empty] | 780 | 1108 | 2.345 | 9.422 | 120.449 | 31.803
Bergshausen - Borken 2 | 11TD2L000000262Y | TENNETGMBH | Bergshausen | Borken | 400 | [7 empty] | 2616 | 3150 | 0.889 | 7.353 | 137.109 | 29.726
Y-Voerden (-Bergshausen - Grohnde) 1 | 11T0-0000-1039-K | TENNETGMBH | Bergshausen | Y-Voerden | 400 | [7 empty] | 2616 | 3150 | 2.338 | 20.132 | 353.583 | 79.697
Y-Wuergassen (-Bergshausen - Sandershausen/O) 2 | 11T0-0000-1073-M | TENNETGMBH | Bergshausen | Wuergassen | 400 | [7 empty] | 2616 | 3150 | 0.341 | 2.887 | 50.856 | 11.384
Bergshausen - Borken 1 | 11TD2L000000024D | TENNETGMBH | Borken | Bergshausen | 400 | [7 empty] | 2616 | 3150 | 0.877 | 7.554 | 132.67 | 29.725
Borken - Giessen/N 2 | 11TD2L0000000293 | TENNETGMBH | Borken | Giessen/N | 400 | [6 empty] | 2947 |  |  | 2.14 | 18.42 | 323.584 | 72.338
Borken - Giessen/N 1 | 11TD2L0000000285 | TENNETGMBH | Borken | Giessen/N | 400 | [6 empty] | 3150 |  |  | 2.14 | 18.42 | 323.584 | 72.369
Borken - Mecklar 2 | 11TD2L000000031G | TENNETGMBH | Borken | Mecklar | 400 | [6 empty] | 2616 |  |  | 1.144 | 10.199 | 185.97 | 40.855
Brunsbuettel - Buettel blau | 11TD2L0000000374 | TENNETGMBH | Buettel | Brunsbuettel | 400 | [6 empty] | 2216 |  |  | 0.115 | 1.51 | 19.666 | 5.331
Brunsbuettel - Buettel gruen | 11TD2L0000000382 | TENNETGMBH | Buettel | Brunsbuettel | 400 | [6 empty] | 2216 |  |  | 0.115 | 1.51 | 19.666 | 5.38
Conneforde - Cloppenburg/O rot | 11TD2L0000000463 | TENNETGMBH | Cloppenburg | Conneforde | 220 | [7 empty] | 759 | 949 | 3.754 | 21.434 | 204.141 | 55.751
Conneforde - Cloppenburg/O gruen | 11TD2L0000000455 | TENNETGMBH | Cloppenburg | Conneforde | 220 | [7 empty] | 706 | 706 | 3.753 | 21.53 | 204.109 | 55.741
Conneforde - Conneforde/O rot | 11T0-0000-0999-V | TENNETGMBH | Conneforde | Conneforde/O | 400 | [6 empty] | 4000 |  |  | 0.001 | 0.1 | 0.515 | 0.098
Conneforde - Diele rot | 11TD2L0000000471 | TENNETGMBH | Conneforde | Diele | 400 | [6 empty] | 2216 |  |  | 1.473 | 16.643 | 219.519 | 56.633
Fedderwarden - Conneforde/O gruen | 11T0-0000-1489-H | TENNETGMBH | Conneforde | Fedderwarden | 400 | [6 empty] | 2570 |  |  | 0.364 | 6.535 | 872.961 | 34.94
Conneforde - Conneforde/O blau | 11T0-0000-0079-A | TENNETGMBH | Conneforde | Conneforde/O | 400 | [6 empty] | 4000 |  |  | 0.001 | 0.1 | 0.515 | 0.098
Conneforde - Diele weiss | 11TD2L000000049Y | TENNETGMBH | Conneforde | Diele | 400 | [6 empty] | 2216 |  |  | 1.473 | 16.647 | 219.591 | 56.648
Fedderwarden - Conneforde/O gelb | 11T0-0000-1488-K | TENNETGMBH | Conneforde | Fedderwarden | 400 | [6 empty] | 2216 |  |  | 0.365 | 6.531 | 898.772 | 34.939
Conneforde - Conneforde/O 422 | 11T0-0000-0031-D | TENNETGMBH | Conneforde | Conneforde/O | 220 | [6 empty] | 1412 |  |  | 0.004 | 0.1 | 24.693 | 0.289
Y-Emden/O (-Conneforde - Emden/Borssum - Emden/O) weiss | 11T0-0000-1101-E | TENNETGMBH | Conneforde | Y-Emden/O | 220 | [6 empty] | 1103 |  |  | 3.854 | 22.027 | 193.616 | 56.209
Conneforde - Conneforde/O 421 | 11T0-0000-1499-D | TENNETGMBH | Conneforde | Conneforde/O | 220 | [6 empty] | 2216 |  |  | 0.004 | 0.1 | 24.693 | 0.005
Conneforde - Fedderwarden blau | 11T0-0000-1614-D | TENNETGMBH | Conneforde | Fedderwarden | 220 | [6 empty] | 2216 |  |  | 0.691 | 8.234 | 115.765 | 28.877
Conneforde/O - Conneforde 423 | 11T0-0000-1500-Y | TENNETGMBH | Conneforde | Conneforde/O | 220 | [6 empty] | 2039 |  |  | 0.001 | 0.1 | 2.199 | 0.023
Conneforde - Fedderwarden rot | 11T0-0000-1613-G | TENNETGMBH | Conneforde | Fedderwarden | 220 | [6 empty] | 2216 |  |  | 0.691 | 8.231 | 115.84 | 28.869
Unterweser - Conneforde rot | 11TD2L0000002350 | TENNETGMBH | Conneforde | Unterweser | 220 | [6 empty] | 1898 |  |  | 0.835 | 9.348 | 121.266 | 31.636
Y-Emden/O (-Conneforde - Emden/Borssum - Emden/O) schwarz | 11T0-0000-1097-2 | TENNETGMBH | Conneforde | Y-Emden/O | 220 | [6 empty] | 1103 |  |  | 3.726 | 21.678 | 196.89 | 56.209
Conneforde/O - Unterweser gelb | 11TD2L0000002342 | TENNETGMBH | Conneforde/O | Unterweser | 400 | [6 empty] | 2216 |  |  | 0.816 | 9.404 | 122.265 | 31.538
Diele - Doerpen/W gelb | 11TD2L0000000536 | TENNETGMBH | Diele | Doerpen/W | 400 | [6 empty] | 2216 |  |  | 0.484 | 5.424 | 70.299 | 18.356
Dipperz - Grosskrotzenburg 2 | 11TD2L000000337T | TENNETGMBH | Dipperz | Grosskrotzenburg | 400 | [6 empty] | 2204 |  |  | 2.459 | 22.654 | 397.883 | 89.153
Dipperz - Grosskrotzenburg 1 | 11TD2L000000102J | TENNETGMBH | Dipperz | Grosskrotzenburg | 400 | [6 empty] | 2204 |  |  | 2.459 | 22.654 | 397.883 | 89.139
Y-Alfstedt (-Dollern - Elsfleth/W) schwarz | 11T0-0000-1114-1 | TENNETGMBH | Dollern | Y-Alfstedt | 400 | [6 empty] | 2216 |  |  | 0.854 | 9.56 | 123.948 | 32.344
Bechterdissen - Elsen 2 | 11TD2L000000335X | TENNETGMBH | Elsen | Bechterdissen | 400 | [7 empty] | 2748 | 3150 | 0.883 | 8.115 | 143.131 | 31.945
Elsen - Twistetal 2 | 11TD2L0000002318 | TENNETGMBH | Elsen | Twistetal | 400 | [7 empty] | 2720 | 3150 | 1.497 | 13.809 | 240.929 | 54.192
Bechterdissen - Elsen 1 | 11TD2L000000017A | TENNETGMBH | Elsen | Bechterdissen | 400 | [7 empty] | 2720 | 3150 | 0.886 | 8.049 | 144.366 | 31.954
Elsen - Twistetal 1 | 11TD2L0000002326 | TENNETGMBH | Elsen | Twistetal | 400 | [7 empty] | 2720 | 3150 | 1.497 | 13.797 | 241.306 | 54.194
Eltmann - Redwitz 428 | 11TD2L000000088O | TENNETGMBH | Eltmann | Redwitz | 400 | [6 empty] | 3154 |  |  | 1.2561 | 14.359 | 257.4975 | 58.2727
Elsfleth/W - Niedervieland gruen | 11T0-0000-1003-D | TENNETGMBH | Elsfleth/W | Niedervieland | 400 | [6 empty] | 2216 |  |  | 0.763 | 8.962 | 119.208 | 30.638
Elsfleth/W - Farge gruen | 11T0-0000-1005-7 | TENNETGMBH | Elsfleth/W | Farge | 400 | [6 empty] | 2216 |  |  | 0.225 | 2.673 | 37.209 | 9.5
Elsfleth/W - Ganderkesee rot | 11T0-0000-0982-J | TENNETGMBH | Elsfleth/W | Ganderkesee | 400 | [6 empty] | 2216 |  |  | 0.759 | 8.809 | 111.212 | 29.392
Y-Emden/O (-Emden/Borssum - Conneforde) schwarz | 11T0-0000-1095-8 | TENNETGMBH | Emden/Borssum | Y-Emden/O | 220 | [6 empty] | 1103 |  |  | 0.072 | 0.412 | 3.16 | 1.07
Y-Emden/O (-Emden/Borssum - Conneforde) weiss | 11T0-0000-1099-X | TENNETGMBH | Emden/Borssum | Y-Emden/O | 220 | [6 empty] | 1103 |  |  | 0.072 | 0.412 | 3.16 | 1.068
Conneforde - Emden/O gelb | 11T0-0000-1677-H | TENNETGMBH | Emden/O | Conneforde | 400 | [6 empty] | 2570 |  |  | 0.7576 | 13.75 | 1042.249 | 65.0318
Conneforde/O - Emden/O blau | 11T0-0000-1678-E | TENNETGMBH | Emden/O | Conneforde/O | 400 | [6 empty] | 2570 |  |  | 0.7659 | 13.913 | 1060.822 | 65.5902
Y-Emden/O (-Emden/O - Emden/Borssum - Conneforde) schwarz | 11T0-0000-1096-5 | TENNETGMBH | Emden/O | Y-Emden/O | 220 | [6 empty] | 1299 |  |  | 0.028 | 0.1 | 57.56 | 1.301
Y-Emden/O (-Emden/O - Emden/Borssum - Conneforde) weiss | 11T0-0000-1100-H | TENNETGMBH | Emden/O | Y-Emden/O | 220 | [6 empty] | 1299 |  |  | 0.072 | 0.305 | 30.631 | 0.393
Y-Erzhausen (-Erzhausen - Godenau - Hardegsen - Goettingen) 3 | 11T0-0000-1035-W | TENNETGMBH | Erzhausen | Y-Erzhausen | 220 | [6 empty] | 834 |  |  | 0.46 | 2.2 | 15.708 | 5.2
Y-Erzhausen (-Erzhausen - Hardegsen - Lehrte) 2 | 11T0-0000-1110-D | TENNETGMBH | Erzhausen | Y-Erzhausen | 220 | [6 empty] | 834 |  |  | 0.443 | 2.042 | 15.02 | 5.196
Etzenricht - Mechlenreuth 437 | 11T0-0000-0103-E | TENNETGMBH | Etzenricht | Mechlenreuth | 400 | [7 empty] | 2206 | 3115 | 2.321 | 26.271 | 338.255 | 88.228
Etzenricht - Schwandorf 248 | 11TD2L000000176R | TENNETGMBH | Etzenricht | Schwandorf | 220 | [7 empty] | 1102 | 1274 | 2.26 | 17.208 | 121.806 | 44.177
Y-Alfstedt (-Farge - Dollern) blau | 11T0-0000-1068-B | TENNETGMBH | Farge | Y-Alfstedt | 400 | [6 empty] | 2216 |  |  | 1.561 | 17.973 | 233.678 | 58.771
Fedderwarden - Maade weiss | 11T0-0000-1615-A | TENNETGMBH | Fedderwarden | Maade | 220 | [6 empty] | 2216 |  |  | 0.13 | 1.495 | 20.455 | 5.169
Fedderwarden - Maade schwarz | 11T0-0000-1616-7 | TENNETGMBH | Fedderwarden | Maade | 220 | [6 empty] | 2216 |  |  | 0.13 | 1.493 | 20.524 | 5.17
Y-Doernigheim (-Frankfurt/N - Grosskrotzenburg) 1 | 11T0-0000-1042-0 | TENNETGMBH | Frankfurt/N | Y-Doernigheim | 220 | [6 empty] | 1250 |  |  | 0.787 | 3.763 | 49.951 | 12.944
Y-Doernigheim (-Frankfurt/N - Grosskrotzenburg) 2 | 11T0-0000-1045-S | TENNETGMBH | Frankfurt/N | Y-Doernigheim | 220 | [6 empty] | 1250 |  |  | 0.787 | 3.763 | 49.951 | 12.944
Giessen/N - Dillenburg 3 | 11TD2L000000076V | TENNETGMBH | Giessen/N | Dillenburg | 400 | [6 empty] | 2612 |  |  | 1.062 | 9.606 | 168.713 | 37.837
Giessen/N - Karben 2 | 11TD2L0000003144 | TENNETGMBH | Giessen/N | Karben | 400 | [6 empty] | 2612 |  |  | 1.52 | 12.852 | 227.894 | 50.704
Giessen/N - Asslar 4 | 11TD2L000000075X | TENNETGMBH | Giessen/N | Asslar | 400 | [6 empty] | 2612 |  |  | 0.403 | 3.467 | 60.884 | 13.238
Giessen/N - Karben 1 | 11T0-0000-0055-U | TENNETGMBH | Giessen/N | Karben | 400 | [6 empty] | 2616 |  |  | 1.498 | 12.9 | 226.509 | 50.704
Bergrheinfeld/W - Grosskrotzenburg 417 | 11T0-0000-0045-Y | TENNETGMBH | Grosskrotzenburg | Bergrheinfeld/W | 400 | [6 empty] | 2616 |  |  | 2.88 | 30.645 | 470.526 | 112.758
Aschaffenburg - Grosskrotzenburg 412 | 11TD2L000000006F | TENNETGMBH | Grosskrotzenburg | Aschaffenburg | 400 | [6 empty] | 2619 |  |  | 0.756 | 8.381 | 121.328 | 29.834
Grosskrotzenburg - Frankfurt/N 3 | 11TD2L000000101L | TENNETGMBH | Grosskrotzenburg | Frankfurt/N | 220 | [6 empty] | 1250 |  |  | 1.268 | 6.32 | 84.415 | 21.607
Grosskrotzenburg - Trennfeld 217 | 11TD2L000000103H | TENNETGMBH | Grosskrotzenburg | Trennfeld | 220 | [7 empty] | 834 | 1105 | 6.39 | 28.892 | 229.336 | 75.85
Y-Doernigheim (-Grosskrotzenburg - Frankfurt/N) 2 | 11T0-0000-1043-Y | TENNETGMBH | Grosskrotzenburg | Y-Doernigheim | 220 | [6 empty] | 1250 |  |  | 0.535 | 2.558 | 34.558 | 8.731
Grosskrotzenburg - Trennfeld 218 | 11TD2L000000104F | TENNETGMBH | Grosskrotzenburg | Trennfeld | 220 | [7 empty] | 834 | 1105 | 6.39 | 28.892 | 229.336 | 76.253
Y-Doernigheim (-Grosskrotzenburg - Frankfurt/N) 1 | 11T0-0000-1040-6 | TENNETGMBH | Grosskrotzenburg | Y-Doernigheim | 220 | [6 empty] | 1250 |  |  | 0.535 | 2.558 | 34.558 | 8.693
Wuergassen - Goettingen 4 | 11T0-0000-0036-Z | TENNETGMBH | Goettingen | Wuergassen | 220 | [6 empty] | 834 |  |  | 5.509 | 26.653 | 270.331 | 78.495
Wuergassen - Goettingen 3 | 11T0-0000-0035-1 | TENNETGMBH | Goettingen | Wuergassen | 220 | [6 empty] | 834 |  |  | 5.509 | 26.653 | 270.388 | 78.468
Dollern - Goetzdorf gruen | 11T0-0000-1464-3 | TENNETGMBH | Goetzdorf | Dollern | 220 | [6 empty] | 1647 |  |  | 0.726 | 5.048 | 75.86 | 22.944
Dollern - Goetzdorf blau | 11T0-0000-0038-T | TENNETGMBH | Goetzdorf | Dollern | 220 | [6 empty] | 1628 |  |  | 0.902 | 5.744 | 122.965 | 23.294
Bergrheinfeld/W - Grafenrheinfeld 427 | 11TD2L000000359J | TENNETGMBH | Grafenrheinfeld | Bergrheinfeld/W | 400 | [6 empty] | 2880 |  |  | 0.068 | 0.772 | 14.451 | 3.157
Bergrheinfeld/W - Grafenrheinfeld 487 | 11T0-0000-1675-N | TENNETGMBH | Grafenrheinfeld | Bergrheinfeld/W | 400 | [6 empty] | 2400 |  |  | 0.0688 | 0.7942 | 14.3885 | 3.1883
Grafenrheinfeld - Oberhaid 423 | 11TD2L000000085U | TENNETGMBH | Grafenrheinfeld | Oberhaid | 400 | [6 empty] | 3216 |  |  | 1.07 | 12.378 | 225.211 | 49.557
Grafenrheinfeld - Raitersaich 434 | 11TD2L000000087Q | TENNETGMBH | Grafenrheinfeld | Raitersaich | 400 | [6 empty] | 2400 |  |  | 2 | 21.703 | 405.265 | 88.028
Bergrheinfeld/W - Grafenrheinfeld 426 | 11T0-0000-0029-U | TENNETGMBH | Grafenrheinfeld | Bergrheinfeld/W | 400 | [6 empty] | 2880 |  |  | 0.068 | 0.772 | 14.445 | 3.135
Eltmann - Grafenrheinfeld 422 | 11TD2L0000000641 | TENNETGMBH | Grafenrheinfeld | Eltmann | 400 | [6 empty] | 3216 |  |  | 0.78 | 8.83 | 161.164 | 35.447
Klein Ilsede - Grohnde 1 | 11TD2L0000001354 | TENNETGMBH | Grohnde | Klein Ilsede | 400 | [7 empty] | 2720 | 3150 | 2.126 | 19.4 | 345.896 | 78.837
Algermissen - Grohnde 2 | 11TD2L000000002N | TENNETGMBH | Grohnde | Algermissen | 400 | [7 empty] | 2720 | 3150 | 1.485 | 13.565 | 241.79 | 53.793
Hamburg/N - Brokdorf blau | 11TD2L000000105D | TENNETGMBH | Hamburg/N | Brokdorf | 220 | [7 empty] | 732 | 915 | 3.482 | 18.99 | 145.767 | 49.118
Hamburg/N - Itzehoe/W rot | 11TD2L000000106B | TENNETGMBH | Hamburg/N | Itzehoe/W | 220 | [7 empty] | 732 | 915 | 3.72 | 20.062 | 153.998 | 51.81
Schuby/W - Handewitt gelb | 11T0-0000-1472-5 | TENNETGMBH | Handewitt | Schuby/W | 400 | [6 empty] | 3349 |  |  | 0.354 | 6.459 | 125.739 | 26.8
Audorf/S - Handewitt blau | 11T0-0000-1517-9 | TENNETGMBH | Handewitt | Audorf/S | 400 | [6 empty] | 2216 |  |  | 1.737 | 19.862 | 256.235 | 67.055
Schuby/W - Handewitt rot | 11T0-0000-1471-8 | TENNETGMBH | Handewitt | Schuby/W | 400 | [6 empty] | 3349 |  |  | 0.354 | 6.459 | 125.739 | 26.8
Goettingen - Hardegsen 3 | 11TD2L0000000803 | TENNETGMBH | Hardegsen | Goettingen | 220 | [7 empty] | 667 | 834 | 1.26 | 6.35 | 43.982 | 15.462
Hardegsen - Goettingen 1 | 11T0-0000-0997-0 | TENNETGMBH | Hardegsen | Goettingen | 220 | [6 empty] | 667 |  |  | 1.295 | 6.179 | 42.509 | 15.203
Y-Erzhausen (-Hardegsen - Lehrte) 2 | 11T0-0000-1111-A | TENNETGMBH | Hardegsen | Y-Erzhausen | 220 | [7 empty] | 667 | 834 | 2.613 | 12.876 | 82.668 | 30.599
Hattorf - Helmstedt 2 | 11TD2L0000001095 | TENNETGMBH | Hattorf | Helmstedt | 400 | [7 empty] | 2748 | 3000 | 0.714 | 6.512 | 118.658 | 26.136
Wahle - Helmstedt 1 | 11TD2L000000245Y | TENNETGMBH | Wahle | Helmstedt | 400 | [7 empty] | 2748 | 3150 | 0.714 | 6.512 | 118.658 | 62.318
Suederdonn - Heide/W blau | 11T0-0000-0971-Q | TENNETGMBH | Heide/W | Suederdonn | 400 | [6 empty] | 3349 |  |  | 0.303 | 5.469 | 105.086 | 22.621
Suederdonn - Heide/W gruen | 11T0-0000-0970-T | TENNETGMBH | Heide/W | Suederdonn | 400 | [6 empty] | 3349 |  |  | 0.303 | 5.469 | 105.086 | 22.619
Siems - Herrenwyk/Baltic Cable gelb | 11TD2L0000002148 | TENNETGMBH | Herrenwyk | Siems | 400 | [6 empty] | 1699 |  |  | 0.074 | 0.93 | 12.566 | 3.479
Heide/W - Husum/N weiss | 11T0-0000-1635-2 | TENNETGMBH | Husum/N | Heide/W | 400 | [6 empty] | 3349 |  |  | 0.611 | 11.021 | 214.1 | 45.842
Heide/W - Husum/N schwarz | 11T0-0000-1634-5 | TENNETGMBH | Husum/N | Heide/W | 400 | [6 empty] | 3349 |  |  | 0.611 | 11.021 | 214.1 | 45.843
Ingolstadt - Raitersaich 266 | 11TD2L0000001168 | TENNETGMBH | Ingolstadt | Raitersaich | 220 | [6 empty] | 1103 |  |  | 4.557 | 34.542 | 256.1 | 92.944
Ingolstadt - Raitersaich 265 | 11TD2L000000115A | TENNETGMBH | Ingolstadt | Raitersaich | 220 | [6 empty] | 1102 |  |  | 4.835 | 36.648 | 271.688 | 92.946
Maade - Inhausen schwarz | 11TD2L000000168Q | TENNETGMBH | Inhausen | Maade | 220 | [6 empty] | 1440 |  |  | 0.215 | 2.509 | 31.63 | 8.361
Irsching - Raitersaich 425 | 11TD2L000000121F | TENNETGMBH | Irsching | Raitersaich | 400 | [6 empty] | 2204 |  |  | 2.435 | 26.763 | 494.729 | 100.789
Irsching - Ottenhofen 421 | 11TD2L0000001192 | TENNETGMBH | Irsching | Ottenhofen | 400 | [6 empty] | 2204 |  |  | 2.09 | 22.738 | 291.226 | 76.162
Irsching - Raitersaich 424 | 11TD2L000000120H | TENNETGMBH | Irsching | Raitersaich | 400 | [6 empty] | 2204 |  |  | 2.435 | 26.763 | 494.729 | 100.732
Isar - Ottenhofen 444 | 11TD2L0000001249 | TENNETGMBH | Isar | Ottenhofen | 400 | [6 empty] | 2400 |  |  | 1.41 | 17.291 | 256.668 | 61.314
Isar - Ottenhofen 443 | 11TD2L000000123B | TENNETGMBH | Isar | Ottenhofen | 400 | [6 empty] | 2400 |  |  | 1.41 | 17.295 | 250.071 | 61.314
Isar - Pleinting 451 | 11TD2L0000001265 | TENNETGMBH | Isar | Pleinting | 400 | [6 empty] | 2400 |  |  | 1.43 | 15.587 | 287.142 | 63.465
Isar - Ottenhofen 446 | 11TD2L0000001257 | TENNETGMBH | Isar | Ottenhofen | 400 | [6 empty] | 2400 |  |  | 1.35 | 16.677 | 266.093 | 61.32
Isar - Pleinting 452 | 11TD2L0000001273 | TENNETGMBH | Isar | Pleinting | 400 | [6 empty] | 2400 |  |  | 1.43 | 15.587 | 287.142 | 63.465
Isar - Isar 405 | 11TD2L0000001281 | TENNETGMBH | Isar | Isar | 400 | [6 empty] | 2112 |  |  | 0.1 | 0.1 | 0 | 0.651
Isar - Isar 406 | 11TD2L000000130E | TENNETGMBH | Isar | Isar | 400 | [6 empty] | 2112 |  |  | 0.1 | 0.1 | 0 | 0.651
Brokdorf - Itzehoe/W gruen | 11TD2L000000034A | TENNETGMBH | Itzehoe/W | Brokdorf | 220 | [6 empty] | 915 |  |  | 1.508 | 8.448 | 64.842 | 21.873
Brunsbuettel - Itzehoe/W rot | 11TD2L0000000390 | TENNETGMBH | Itzehoe/W | Brunsbuettel | 220 | [6 empty] | 1699 |  |  | 0.475 | 5.551 | 69.985 | 18.254
Handewitt - Jardelund gruen | 11T0-0000-0925-Y | TENNETGMBH | Jardelund | Handewitt | 400 | [6 empty] | 2216 |  |  | 0.422 | 4.724 | 61.164 | 15.958
Handewitt - Jardelund blau | 11T0-0000-0926-V | TENNETGMBH | Jardelund | Handewitt | 400 | [6 empty] | 2216 |  |  | 0.422 | 4.724 | 61.164 | 15.972
Frankfurt/SW - Karben 3 | 11TD2L0000000730 | TENNETGMBH | Karben | Frankfurt/SW | 400 | [6 empty] | 2204 |  |  | 0.774 | 6.851 | 120.323 | 26.855
Grosskrotzenburg - Karben 3 | 11TD2L0000003136 | TENNETGMBH | Karben | Grosskrotzenburg | 400 | [6 empty] | 2616 |  |  | 0.587 | 4.94 | 88.291 | 19.602
Grosskrotzenburg - Karben 1 | 11TD2L0000003128 | TENNETGMBH | Karben | Grosskrotzenburg | 400 | [6 empty] | 2616 |  |  | 0.587 | 4.94 | 88.291 | 19.663
Kuehtai - Silz 264 | 11T0-0000-1684-M | TENNETGMBH | Kuehtai | Silz | 220 | [6 empty] | 9999 |  |  | 0.5 | 2.84 | 32.717 | 9.08
Kuehtai - Silz 265 | 11T0-0000-1685-J | TENNETGMBH | Kuehtai | Silz | 220 | [6 empty] | 9999 |  |  | 0.5 | 2.84 | 32.717 | 9.085
Audorf/S - Kiel/S gelb/421 | 11T0-0000-1622-F | TENNETGMBH | Kiel/S | Audorf/S | 220 | [6 empty] | 949 |  |  | 2.1177 | 12.232 | 93.8865 | 31.9883
Kiel/W - Kiel/S blau | 11TD2L0000001346 | TENNETGMBH | Kiel/W | Kiel/S | 220 | [6 empty] | 949 |  |  | 1.297 | 7.492 | 57.491 | 19.34
Audorf/S - Kiel/W rot/422 | 11T0-0000-1621-I | TENNETGMBH | Kiel/W | Audorf/S | 220 | [6 empty] | 949 |  |  | 1.6498 | 9.531 | 73.152 | 25.0757
Wahle - Klein Ilsede 3 | 11TD2L000000246W | TENNETGMBH | Klein Ilsede | Wahle | 400 | [7 empty] | 2720 | 3150 | 0.259 | 2.333 | 42.192 | 9.208
Y-Kruen (-Kruen - Oberbrunn - Silz) 250 | 10T1001C--00069I | TENNETGMBH | Kruen | Y-Kruen | 220 | [6 empty] | 1247 |  |  | 0.03 | 0.269 | 2.513 | 0.741
Y-Kruen (-Kruen - Oberbrunn - Silz) 251 | 11T0-0000-1014-6 | TENNETGMBH | Kruen | Y-Kruen | 220 | [6 empty] | 1247 |  |  | 0.03 | 0.269 | 2.513 | 0.741
Kriegenbrunn - Raitersaich 438 | 11TD2L0000001362 | TENNETGMBH | Kriegenbrunn | Raitersaich | 400 | [6 empty] | 2206 |  |  | 0.756 | 6.898 | 123.169 | 27.381
Stadorf - Kruemmel blau/2 | 11TD2L0000002261 | TENNETGMBH | Kruemmel | Stadorf | 400 | [6 empty] | 2400 |  |  | 1.452 | 13.58 | 238.478 | 53.466
Kummerfeld - Dollern gruen | 11T0-0000-0969-6 | TENNETGMBH | Kummerfeld | Dollern | 400 | [6 empty] | 3154 |  |  | 0.415 | 7.13 | 120.131 | 27.469
Veltheim - Lage A06 | 11TD2L0000003403 | TENNETGMBH | Lage | Veltheim | 220 | [7 empty] | 780 | 1108 | 2.863 | 12.266 | 151.927 | 40.702
Landesbergen - Grohnde 1 | 11TD2L0000001419 | TENNETGMBH | Landesbergen | Grohnde | 400 | [7 empty] | 2620 | 3150 | 2.137 | 18.4 | 322.956 | 72.421
Landesbergen - Grohnde 2 | 11TD2L0000001427 | TENNETGMBH | Landesbergen | Grohnde | 400 | [7 empty] | 2620 | 3150 | 2.137 | 18.402 | 323.201 | 72.427
Landesbergen - Hannover/W 3 | 11TD2L0000001435 | TENNETGMBH | Landesbergen | Hannover/W | 220 | [7 empty] | 1048 | 1200 | 2.552 | 12.718 | 169.888 | 43.243
Landesbergen - Hannover/W 4 | 11TD2L0000001443 | TENNETGMBH | Landesbergen | Hannover/W | 220 | [7 empty] | 1008 | 1008 | 2.552 | 12.718 | 169.888 | 43.249
Lehrte - Landesbergen 1 | 11TD2L000000158T | TENNETGMBH | Landesbergen | Lehrte | 220 | [7 empty] | 1044 | 1200 | 4.38 | 21.84 | 292.168 | 74.386
Hamburg/N - Luebeck rot | 11TD2L0000001087 | TENNETGMBH | Luebeck | Hamburg/N | 220 | [7 empty] | 949 | 1200 | 3.22 | 18.91 | 145.267 | 48.772
Hamburg/N - Luebeck gelb | 11TD2L0000001079 | TENNETGMBH | Luebeck | Hamburg/N | 220 | [7 empty] | 949 | 1200 | 3.22 | 18.91 | 145.267 | 48.775
Lehrte - Godenau 1 | 11TD2L000000157V | TENNETGMBH | Lehrte | Godenau | 220 | [7 empty] | 667 | 834 | 4.04 | 20.36 | 137.288 | 48.611
Ludersheim - Raitersaich 237 | 11TD2L0000001621 | TENNETGMBH | Ludersheim | Raitersaich | 220 | [6 empty] | 1447 |  |  | 1.677 | 7.63 | 224.014 | 78.632
Ludersheim - Sittling 221 | 11TD2L000000165W | TENNETGMBH | Ludersheim | Sittling | 220 | [7 empty] | 1040 | 1102 | 3.36 | 16.867 | 383.903 | 147.064
Kruemmel - Lueneburg gruen | 11TD2L000000166U | TENNETGMBH | Lueneburg | Kruemmel | 400 | [6 empty] | 2748 |  |  | 0.765 | 7.117 | 124.998 | 28.016
Stadorf - Lueneburg 1 | 11TD2L000000228Y | TENNETGMBH | Lueneburg | Stadorf | 400 | [6 empty] | 2748 |  |  | 0.687 | 6.462 | 113.487 | 25.438
Marienberg - Neufinsing 251 | 11TD2L000000172Z | TENNETGMBH | Marienberg | Neufinsing | 220 | [6 empty] | 1102 |  |  | 2.32 | 19.15 | 158.65 | 51.423
Marienberg - Neufinsing 250 | 11TD2L0000001710 | TENNETGMBH | Marienberg | Neufinsing | 220 | [6 empty] | 1102 |  |  | 2.32 | 19.15 | 158.65 | 51.423
Mecklar - Dipperz 2 | 11TD2L000000178N | TENNETGMBH | Mecklar | Dipperz | 400 | [6 empty] | 2204 |  |  | 1.495 | 12.873 | 226.085 | 50.574
Mecklar - Dipperz 1 | 11TD2L000000177P | TENNETGMBH | Mecklar | Dipperz | 400 | [6 empty] | 2204 |  |  | 1.495 | 12.873 | 226.085 | 50.574
Lehrte - Mehrum 1 | 11TD2L000000159R | TENNETGMBH | Mehrum | Lehrte | 220 | [7 empty] | 834 | 1200 | 1.151 | 5.788 | 45.047 | 14.71
Y-Hallendorf (-Mehrum - Gleidingen) 2 | 11T0-0000-1053-U | TENNETGMBH | Mehrum | Y-Hallendorf | 220 | [7 empty] | 667 | 834 | 2.407 | 11.29 | 84.823 | 29.22
Mehrum - Hallendorf 1 | 11TD2L000000181Y | TENNETGMBH | Mehrum | Hallendorf | 220 | [7 empty] | 667 | 834 | 2.5 | 11.76 | 91.42 | 30.605
Lehrte - Mehrum 2 | 11TD2L0000001605 | TENNETGMBH | Mehrum | Lehrte | 220 | [7 empty] | 834 | 1200 | 1.151 | 5.788 | 45.047 | 14.715
Meissen - Veltheim A08 | 11TD2L000000338R | TENNETGMBH | Meissen | Veltheim | 220 | [7 empty] | 780 | 1108 | 0.84 | 3.326 | 42.443 | 11.14
Meissen - Veltheim A09 | 11TD2L000000339P | TENNETGMBH | Meissen | Veltheim | 220 | [7 empty] | 780 | 1108 | 0.84 | 3.326 | 42.443 | 11.137
Neufinsing - Ottenhofen 287 | 11TD2L000000187M | TENNETGMBH | Neufinsing | Ottenhofen | 220 | [6 empty] | 1807 |  |  | 0.15 | 1.564 | 21.363 | 5.453
Neufinsing - Ottenhofen 286 | 11TD2L000000186O | TENNETGMBH | Neufinsing | Ottenhofen | 220 | [6 empty] | 1807 |  |  | 0.15 | 1.564 | 21.363 | 5.447
Neufinsing - Zolling 258 | 11TD2L000000188K | TENNETGMBH | Neufinsing | Zolling | 220 | [6 empty] | 2204 |  |  | 0.89 | 9.742 | 138.544 | 32.77
Ganderkesee - Niedervieland schwarz | 11TD2L000000074Z | TENNETGMBH | Niedervieland | Ganderkesee | 400 | [6 empty] | 2216 |  |  | 0.359 | 4.142 | 61.176 | 15.065
Neufinsing - Oberbachern 264 | 11TD2L000000185Q | TENNETGMBH | Oberbachern | Neufinsing | 220 | [6 empty] | 2000 |  |  | 1.07 | 11.503 | 153.938 | 39.265
Neufinsing - Oberbachern 263 | 11TD2L000000184S | TENNETGMBH | Oberbachern | Neufinsing | 220 | [6 empty] | 2000 |  |  | 1.07 | 11.503 | 153.938 | 39.265
Oberbachern - Oberbrunn 270 | 11TD2L000000194P | TENNETGMBH | Oberbrunn | Oberbachern | 220 | [6 empty] | 2000 |  |  | 0.84 | 9.469 | 115.297 | 30.918
Y-Kruen (-Oberbrunn - Silz) 250 | 10T1001C--00070X | TENNETGMBH | Oberbrunn | Y-Kruen | 220 | [6 empty] | 2124 |  |  | 1.78 | 21.994 | 251.013 | 71.411
Oberbachern - Oberbrunn 269 | 11TD2L000000193R | TENNETGMBH | Oberbrunn | Oberbachern | 220 | [6 empty] | 2000 |  |  | 0.84 | 9.469 | 115.297 | 30.919
Y-Kruen (-Oberbrunn - Silz) 251 | 11T0-0000-1013-9 | TENNETGMBH | Oberbrunn | Y-Kruen | 220 | [6 empty] | 2124 |  |  | 1.78 | 21.994 | 251.013 | 71.411
Oberhaid - Redwitz 435 | 11TD2L000000197J | TENNETGMBH | Oberhaid | Redwitz | 400 | [6 empty] | 3220 |  |  | 0.94 | 10.61 | 194.779 | 43.33
Oberbachern - Ottenhofen 462 | 11TD2L000000196L | TENNETGMBH | Ottenhofen | Oberbachern | 400 | [6 empty] | 2204 |  |  | 1.2 | 13.127 | 166.819 | 44.118
Oberbachern - Ottenhofen 461 | 11TD2L000000195N | TENNETGMBH | Ottenhofen | Oberbachern | 400 | [6 empty] | 2204 |  |  | 1.2 | 13.127 | 166.819 | 44.163
Landesbergen - Ohlensehlen 1 | 11TD2L0000003322 | TENNETGMBH | Ohlensehlen | Landesbergen | 400 | [6 empty] | 2360 |  |  | 0.496 | 4.267 | 74.77 | 16.71
Ovenstaedt - Eickum 4 | 11TD2L000000199F | TENNETGMBH | Ovenstaedt | Eickum | 400 | [6 empty] | 3126 |  |  | 1.248 | 11.452 | 202.253 | 45.381
Landesbergen - Ovenstaedt 4 | 11TD2L000000149U | TENNETGMBH | Ovenstaedt | Landesbergen | 400 | [7 empty] | 2620 | 3150 | 0.716 | 6.482 | 113.851 | 25.688
Ovenstaedt - Eickum 3 | 11T0-0000-1547-Y | TENNETGMBH | Ovenstaedt | Eickum | 400 | [6 empty] | 3126 |  |  | 1.248 | 11.452 | 202.253 | 45.304
Ovenstaedt - Sottrum 3 | 11TD2L000000200J | TENNETGMBH | Ovenstaedt | Sottrum | 400 | [7 empty] | 2216 | 3150 | 2.76 | 30.01 | 420.973 | 104.959
Y-Plattling (-Plattling - Pleinting - Schwandorf) 465 | 11T0-0000-1060-Z | TENNETGMBH | Plattling | Y-Plattling | 400 | [6 empty] | 816 |  |  | 0.01 | 0.1 | 3.142 | 0.115
Y-Plattling (-Pleinting - Schwandorf) 465 | 11T0-0000-1059-C | TENNETGMBH | Pleinting | Y-Plattling | 400 | [6 empty] | 2204 |  |  | 0.635 | 7 | 89.85 | 23.217
Pirach - Pleinting 257 | 11TD2L000000201H | TENNETGMBH | Pleinting | Pirach | 220 | [7 empty] | 1360 | 2000 | 4.769 | 25.987 | 328.504 | 86.119
Raitersaich - Wuergau 431 | 11TD2L0000002067 | TENNETGMBH | Raitersaich | Wuergau | 400 | [6 empty] | 2748 |  |  | 2.309 | 20.282 | 374.013 | 81.255
Raitersaich - Trennfeld 211 | 11TD2L0000002075 | TENNETGMBH | Raitersaich | Trennfeld | 220 | [6 empty] | 1492 |  |  | 5.065 | 26.435 | 577.34 | 229.808
Kriegenbrunn - Redwitz 432 | 11TD2L0000001370 | TENNETGMBH | Redwitz | Kriegenbrunn | 400 | [6 empty] | 2206 |  |  | 2.158 | 20.365 | 364.494 | 80.82
Mechlenreuth - Redwitz 469 | 11T0-0000-0104-B | TENNETGMBH | Redwitz | Mechlenreuth | 400 | [7 empty] | 2204 | 3150 | 1.296 | 14.666 | 188.879 | 49.314
Y-Rhede (-Rhede - Diele - Doerpen/W) schwarz | 11T0-0000-1019-S | TENNETGMBH | Rhede | Y-Rhede | 400 | [6 empty] | 150 |  |  | 0.481 | 5.538 | 72.004 | 0.023
Y-Wuergassen (-Sandershausen/O - Bergshausen) 2 | 11T0-0000-1072-P | TENNETGMBH | Sandershausen/O | Wuergassen | 400 | [6 empty] | 320 |  |  | 0.001 | 0.1 | 0.075 | 0.025
Y-Plattling (-Schwandorf - Pleinting) 465 | 11T0-0000-1061-W | TENNETGMBH | Schwandorf | Y-Plattling | 400 | [6 empty] | 2204 |  |  | 2.445 | 26.98 | 341.177 | 89.42
Ludersheim - Schwandorf 223 | 11TD2L000000164Y | TENNETGMBH | Schwandorf | Ludersheim | 220 | [6 empty] | 1094 |  |  | 4.931 | 18.545 | 239.829 | 63.425
Pleinting - Schwandorf 226 | 11TD2L000000204B | TENNETGMBH | Schwandorf | Pleinting | 220 | [6 empty] | 1102 |  |  | 6.16 | 45.833 | 317.929 | 112.554
Etzenricht - Schwandorf 457 | 11TD2L0000000706 | TENNETGMBH | Schwandorf | Etzenricht | 400 | [6 empty] | 2484 |  |  | 1.18 | 12.832 | 164.305 | 42.951
Schwandorf - Schwandorf 497 | 11T0-0000-1493-V | TENNETGMBH | Schwandorf | Schwandorf | 400 | [6 empty] | 2204 |  |  | 0.1 | 0.1 | 0 | 0.695
Brunsbuettel - Suederdonn blau | 11TD2L000000344W | TENNETGMBH | Suederdonn | Brunsbuettel | 400 | [6 empty] | 3349 |  |  | 0.193 | 3.491 | 64.403 | 14.103
Brunsbuettel - Suederdonn gelb | 11TD2L000000343Y | TENNETGMBH | Suederdonn | Brunsbuettel | 400 | [6 empty] | 3349 |  |  | 0.196 | 3.543 | 65.345 | 14.187
Audorf/S - Schuby/W schwarz | 11T0-0000-1475-X | TENNETGMBH | Schuby/W | Audorf/S | 400 | [6 empty] | 3349 |  |  | 0.552 | 9.879 | 196.925 | 41.64
Audorf/S - Schuby/W weiss | 11T0-0000-1473-2 | TENNETGMBH | Schuby/W | Audorf/S | 400 | [6 empty] | 3349 |  |  | 0.552 | 9.879 | 196.925 | 41.64
Y-Simbach (-Simbach - St. Peter - Altheim) 233/230 | 11T0-0000-0985-A | TENNETGMBH | Simbach | Y-Simbach | 220 | [7 empty] | 1102 | 1200 | 0.207 | 1.58 | 11.168 | 3.961
Y-Simbach (-Simbach - St. Peter - Altheim) 234/230 | 11T0-0000-0987-4 | TENNETGMBH | Simbach | Y-Simbach | 220 | [7 empty] | 1102 | 1200 | 0.2065 | 1.58 | 11.1684 | 3.959
Siems - Luebeck blau | 11TD2L0000002156 | TENNETGMBH | Siems | Luebeck | 220 | [6 empty] | 950 |  |  | 0.16 | 1.1 | 725.708 | 9.993
Ingolstadt - Sittling 228 | 11TD2L0000001184 | TENNETGMBH | Sittling | Ingolstadt | 220 | [6 empty] | 1360 |  |  | 1.36 | 7.311 | 93.305 | 24.388
Ingolstadt - Sittling 227 | 11TD2L0000001176 | TENNETGMBH | Sittling | Ingolstadt | 220 | [6 empty] | 1360 |  |  | 1.36 | 7.311 | 93.305 | 24.376
Y-Kruen (-Silz - Oberbrunn) 250 | 10T1001C--00071V | TENNETGMBH | Silz | Y-Kruen | 220 | [6 empty] | 2080 |  |  | 1.05 | 12.758 | 157.048 | 42.197
Y-Kruen (-Silz - Oberbrunn) 251 | 10T1001C--00059L | TENNETGMBH | Silz | Y-Kruen | 220 | [6 empty] | 2080 |  |  | 1.033 | 12.069 | 167.73 | 42.192
Sottrum - Dollern gruen | 11TD2L0000002180 | TENNETGMBH | Sottrum | Dollern | 400 | [7 empty] | 2216 | 3150 | 1.34 | 15.41 | 201.062 | 52.592
Landesbergen - Sottrum 2 | 11TD2L0000001508 | TENNETGMBH | Sottrum | Landesbergen | 400 | [7 empty] | 2216 | 3150 | 2.032 | 24.247 | 296.252 | 79.141
Sottrum - Dollern schwarz | 11TD2L000000219Z | TENNETGMBH | Sottrum | Dollern | 400 | [7 empty] | 2216 | 3150 | 1.34 | 15.41 | 201.062 | 52.582
Sottrum - Blockland blau | 11TD2L0000002164 | TENNETGMBH | Sottrum | Blockland | 220 | [6 empty] | 949 |  |  | 2.71 | 14.98 | 114.982 | 38.713
Wahle - Stadorf 1 | 11TD2L000000247U | TENNETGMBH | Stadorf | Wahle | 400 | [6 empty] | 2494 |  |  | 2.528 | 21.765 | 382.269 | 85.74
Wahle - Stadorf 2 | 11TD2L000000248S | TENNETGMBH | Stadorf | Wahle | 400 | [6 empty] | 2616 |  |  | 2.528 | 21.765 | 382.269 | 85.798
Dollern - Stade/W weiss | 11T0-0000-1567-Q | TENNETGMBH | Stade/W | Dollern | 400 | [6 empty] | 2598 |  |  | 0.19 | 3.508 | 67.491 | 57.4
Elsfleth/W - Unterweser rot | 11T0-0000-0981-M | TENNETGMBH | Unterweser | Elsfleth/W | 400 | [6 empty] | 2216 |  |  | 0.706 | 7.979 | 104.593 | 27.132
Unterweser - Elsfleth/W weiss | 11T0-0000-1004-A | TENNETGMBH | Unterweser | Elsfleth/W | 400 | [6 empty] | 2216 |  |  | 0.706 | 7.98 | 104.612 | 27.137
Voslapp - Inhausen rot | 11TD2L000000237X | TENNETGMBH | Voslapp | Inhausen | 220 | [6 empty] | 1440 |  |  | 0.066 | 0.768 | 9.682 | 2.524
Maade - Voslapp weiss | 11TD2L000000169O | TENNETGMBH | Voslapp | Maade | 220 | [6 empty] | 1440 |  |  | 0.149 | 1.741 | 21.947 | 5.729
Wahle - Hattorf 2 | 11TD2L0000002431 | TENNETGMBH | Wahle | Hattorf | 400 | [7 empty] | 2748 | 3000 | 0.987 | 9.035 | 162.559 | 36.185
Wahle - Braunschweig/N 1 | 11TD2L000000239T | TENNETGMBH | Wahle | Braunschweig/N | 220 | [7 empty] | 667 | 834 | 0.842 | 4.237 | 31.733 | 10.568
Wahle - Braunschweig/N 2 | 11TD2L0000002407 | TENNETGMBH | Wahle | Braunschweig/N | 220 | [7 empty] | 667 | 834 | 0.842 | 4.237 | 31.733 | 10.574
Wahle - Hallendorf 3 | 11TD2L0000002423 | TENNETGMBH | Wahle | Hallendorf | 220 | [7 empty] | 1088 | 1360 | 0.94 | 4.64 | 62.3606 | 15.9666
Wahle - Gleidingen 2 | 11TD2L0000002415 | TENNETGMBH | Wahle | Gleidingen | 220 | [7 empty] | 1178 | 1360 | 0.36 | 1.83 | 26.358 | 6.545
Lehrte - Wahle 1 | 11TD2L0000001613 | TENNETGMBH | Wahle | Lehrte | 220 | [6 empty] | 834 |  |  | 1.601 | 7.7 | 178.534 | 62.223
Y-Waldeck (-Waldeck - Borken - Twistetal) 3 | 11T0-0000-1016-0 | TENNETGMBH | Waldeck | Y-Waldeck | 400 | [6 empty] | 2400 |  |  | 0.1 | 0.83 | 15.388 | 3.364
Y-Waldeck (-Waldeck - Borken - Twistetal) 2 | 11T0-0000-1466-Y | TENNETGMBH | Waldeck | Y-Waldeck | 400 | [6 empty] | 2400 |  |  | 0.099 | 0.857 | 15.042 | 3.38
Redwitz - Wuergau 436 | 11TD2L000000255V | TENNETGMBH | Wuergau | Redwitz | 400 | [6 empty] | 3154 |  |  | 0.499 | 5.533 | 98.046 | 21.327
Brokdorf - Wilster/W weiss | 11TD2L0000000366 | TENNETGMBH | Wilster/W | Brokdorf | 400 | [6 empty] | 2216 |  |  | 0.208 | 2.399 | 31.187 | 8.195
Buettel - Wilster/W gelb | 11TD2L0000000439 | TENNETGMBH | Wilster/W | Buettel | 400 | [6 empty] | 2620 |  |  | 0.234 | 2.9 | 39.898 | 9.312
Wilster/W - Stade/W gelb | 11T0-0000-1569-K | TENNETGMBH | Wilster/W | Stade/W | 400 | [6 empty] | 2598 |  |  | 1.42 | 18.168 | 259.492 | 62.548
Brokdorf - Wilster/W schwarz | 11TD2L0000000358 | TENNETGMBH | Wilster/W | Brokdorf | 400 | [6 empty] | 2216 |  |  | 0.208 | 2.399 | 31.187 | 8.194
Buettel - Wilster/W rot | 11TD2L0000000447 | TENNETGMBH | Wilster/W | Buettel | 400 | [6 empty] | 2620 |  |  | 0.234 | 2.9 | 39.898 | 9.252
Dollern - Wilster/W rot | 11TD2L000000059V | TENNETGMBH | Wilster/W | Dollern | 400 | [6 empty] | 2794 |  |  | 1.474 | 16.99 | 219.057 | 57.4
Y-Wuergassen (-Wuergassen - Bergshausen - Sandershausen/O) 2 | 11T0-0000-1071-S | TENNETGMBH | Wuergassen | Wuergassen | 400 | [7 empty] | 2620 | 3150 | 1.352 | 11.431 | 203.032 | 45.7648
Grohnde - Wuergassen 2 | 11TD2L000000092X | TENNETGMBH | Wuergassen | Grohnde | 400 | [7 empty] | 2620 | 3150 | 1.674 | 14.412 | 253.118 | 57.347
Y-Alfstedt (-Dollern - Farge) blau | 11T0-0000-1070-V | TENNETGMBH | Y-Alfstedt | Dollern | 400 | [6 empty] | 2216 |  |  | 0.771 | 8.88 | 115.454 | 32.336
Y-Alfstedt (-Elsfleth/W - Dollern) schwarz | 11T0-0000-1112-7 | TENNETGMBH | Y-Alfstedt | Elsfleth/W | 400 | [6 empty] | 2216 |  |  | 1.772 | 20.001 | 261.83 | 67.941
Y-Doernigheim (-Doernigheim - Frankfurt/N - Grosskrotzenburg) 1 | 11T0-0000-1041-3 | TENNETGMBH | Y-Doernigheim | Doernigheim | 220 | [6 empty] | 559 |  |  | 0.006 | 0.1 | 0.314 | 0.082
Y-Doernigheim (-Doernigheim - Frankfurt/N - Grosskrotzenburg) 2 | 11T0-0000-1044-V | TENNETGMBH | Y-Doernigheim | Doernigheim | 220 | [6 empty] | 558 |  |  | 0.006 | 0.1 | 0.314 | 0.082
Y-Erzhausen (-Godenau - Hardegsen - Goettingen) 3 | 11T0-0000-1034-Z | TENNETGMBH | Y-Erzhausen | Godenau | 220 | [7 empty] | 667 | 834 | 1.03 | 5.18 | 35.186 | 13.314
Y-Erzhausen (-Hardegsen - Godenau - Goettingen) 3 | 11T0-0000-1239-A | TENNETGMBH | Y-Erzhausen | Hardegsen | 220 | [7 empty] | 667 | 834 | 2.55 | 12.8 | 87.965 | 30.351
Y-Erzhausen (-Lehrte - Hardegsen) 2 | 11T0-0000-1109-R | TENNETGMBH | Y-Erzhausen | Lehrte | 220 | [7 empty] | 667 | 834 | 5.205 | 25.647 | 164.67 | 60.949
Y-Frankfurt/SW (-Frankfurt/SW - Karben - Kriftel) 2 | 11T0-0000-0988-1 | TENNETGMBH | Y-Frankfurt/SW | Frankfurt/SW | 400 | [6 empty] | 2400 |  |  | 0.158 | 1.326 | 23.493 | 5.637
Y-Frankfurt/SW (-Karben - Kriftel) 2 | 11T0-0000-0989-Z | TENNETGMBH | Y-Frankfurt/SW | Karben | 400 | [6 empty] | 2620 |  |  | 0.628 | 5.498 | 97.933 | 21.203
Y-Hallendorf (-Gleidingen - Mehrum) 2 | 11T0-0000-1054-R | TENNETGMBH | Y-Hallendorf | Gleidingen | 220 | [6 empty] | 1088 |  |  | 0.58 | 2.81 | 36.003 | 8.427
Y-Hallendorf (-Hallendorf - Mehrum - Gleidingen) 2 | 11T0-0000-1055-O | TENNETGMBH | Y-Hallendorf | Hallendorf | 220 | [6 empty] | 960 |  |  | 0.139 | 0.698 | 4.741 | 1.39
Y-Huntorf (-Blockland - Conneforde) weiss | 11T0-0000-1123-0 | TENNETGMBH | Y-Huntorf | Blockland | 220 | [6 empty] | 949 |  |  | 3.402 | 18.983 | 145.468 | 47.427
Y-Huntorf (-Conneforde - Blockland) weiss | 11T0-0000-1121-6 | TENNETGMBH | Y-Huntorf | Conneforde | 220 | [6 empty] | 949 |  |  | 1.76 | 10.165 | 77.991 | 26.344
Y-Huntorf (-Huntorf - Conneforde - Sottrum) weiss | 11T0-0000-1122-3 | TENNETGMBH | Y-Huntorf | Huntorf | 220 | [6 empty] | 949 |  |  | 0.367 | 2.12 | 16.336 | 5.523
Y-Huntorf (-Conneforde - Sottrum) gelb | 11T0-0000-1118-Q | TENNETGMBH | Y-Huntorf | Conneforde | 220 | [6 empty] | 949 |  |  | 1.803 | 10.257 | 79.796 | 26.341
Y-Huntorf (-Huntorf - Conneforde - Sottrum) gelb | 11T0-0000-1119-N | TENNETGMBH | Y-Huntorf | Huntorf | 220 | [6 empty] | 949 |  |  | 0.744 | 4.3 | 33.068 | 5.522
Y-Huntorf (-Sottrum - Conneforde) gelb | 11T0-0000-1120-9 | TENNETGMBH | Y-Huntorf | Sottrum | 220 | [6 empty] | 883 |  |  | 4.631 | 25.778 | 200.12 | 67.317
Y-Niederlangen (-Doerpen/W - Meppen) EOWS | 11T0-0000-0990-L | TENNETGMBH | Y-Niederlangen | Doerpen/W | 400 | [6 empty] | 2575 |  |  | 0.338 | 3.787 | 49.069 | 12.928
Y-Niederlangen (-Niederlangen - Doerpen/W - Meppen) EOWS | 11T0-0000-0991-I | TENNETGMBH | Y-Niederlangen | Niederlangen | 400 | [6 empty] | 750 |  |  | 0.008 | 0.1 | 1.21 | 0.333
Y-Rhede (-Diele - Doerpen/W) schwarz | 11T0-0000-1018-V | TENNETGMBH | Y-Rhede | Diele | 400 | [6 empty] | 2216 |  |  | 0.347 | 3.881 | 50.3 | 13.119
Y-Rhede (-Doerpen/W - Diele) schwarz | 11T0-0000-1020-E | TENNETGMBH | Y-Rhede | Doerpen/W | 400 | [6 empty] | 2216 |  |  | 0.138 | 1.543 | 19.999 | 5.218
Y-Voerden (-Grohnde - Bergshausen) 1 | 11T0-0000-1037-Q | TENNETGMBH | Y-Voerden | Grohnde | 400 | [7 empty] | 2616 | 3150 | 0.84 | 7.231 | 127.005 | 28.938
Y-Voerden (-Voerden - Grohnde - Bergshausen) 1 | 11T0-0000-1038-N | TENNETGMBH | Y-Voerden | Voerden | 400 | [6 empty] | 883 |  |  | 0.015 | 0.127 | 2.199 | 0.258
Y-Waldeck (-Borken - Twistetal) 3 | 11T0-0000-1015-3 | TENNETGMBH | Y-Waldeck | Borken | 400 | [7 empty] | 2720 | 3154 | 0.514 | 4.675 | 84.176 | 18.632
Y-Waldeck (-Twistetal - Borken) 3 | 11T0-0000-1017-Y | TENNETGMBH | Y-Waldeck | Twistetal | 400 | [7 empty] | 2720 | 3154 | 0.6371 | 5.9284 | 104.1187 | 23.3289
Y-Waldeck (-Borken - Twistetal) 2 | 11T0-0000-1465-0 | TENNETGMBH | Y-Waldeck | Borken | 400 | [7 empty] | 2620 | 3150 | 0.55 | 4.735 | 83.152 | 18.639
Y-Wechold (-Landesbergen - Sottrum) rot/1 | 11T0-0000-1049-G | TENNETGMBH | Y-Wechold | Landesbergen | 220 | [7 empty] | 886 | 1108 | 3.346 | 12.87 | 168.468 | 42.692
Y-Wechold (-Sottrum - Landesbergen) rot/1 | 11T0-0000-1052-X | TENNETGMBH | Y-Wechold | Sottrum | 220 | [7 empty] | 886 | 949 | 2.613 | 10.05 | 131.554 | 33.806
Y-Wechold (-Wechold - Landesbergen - Sottrum) rot/1 | 11T0-0000-1050-2 | TENNETGMBH | Y-Wechold | Wechold | 220 | [7 empty] | 886 | 1108 | 0.06 | 0.23 | 3.01 | 0.761
Y-Wechold (-Landesbergen - Sottrum) gelb/2 | 11T0-0000-1046-P | TENNETGMBH | Y-Wechold | Landesbergen | 220 | [7 empty] | 886 | 1108 | 3.346 | 12.87 | 168.468 | 42.612
Y-Wechold (-Sottrum - Landesbergen) gelb/2 | 11T0-0000-1048-J | TENNETGMBH | Y-Wechold | Sottrum | 220 | [7 empty] | 886 | 949 | 2.613 | 10.05 | 131.554 | 33.801
Y-Wechold (-Wechold - Landesbergen - Sottrum) gelb/2 | 11T0-0000-1047-M | TENNETGMBH | Y-Wechold | Wechold | 220 | [7 empty] | 886 | 1108 | 0.06 | 0.23 | 3.01 | 0.766
Irsching - Zolling 262 | 11TD2L000000122D | TENNETGMBH | Zolling | Irsching | 220 | [6 empty] | 1600 |  |  | 1.117 | 12.212 | 155.647 | 40.15
Y-Dauersberg (-Asslar - Limburg) WW1 | 11T0-0000-1238-D | TENNETGMBH | Asslar | Dauersberg | 400 | [6 empty] | 2612 |  |  | 0.515 | 4.514 | 78.54 | 26.164 | Internal tie-line with Amprion
Guetersloh - Bechterdissen SN2 | 11T0-0000-0072-V | TENNETGMBH | Bechterdissen | Guetersloh | 400 | [6 empty] | 2720 |  |  | 0.346 | 3.26 | 59.847 | 26.45 | Internal tie-line with Amprion
Brunsbuettel - Brunsbuettel - Hamburg/N 951 | 11T0-0000-0024-8 | TENNETGMBH | Brunsbuettel | Brunsbuettel | 400 | [6 empty] | 3600 |  |  | 0.007 | 0.106 | 1.791 | 0.584 | Internal tie-line with 50Hertz
Brunsbuettel - Brunsbuettel 949 | 11T-D2-D8-000027 | TENNETGMBH | Brunsbuettel | Brunsbuettel | 400 | [6 empty] | 2216 |  |  | 0.005 | 0.1 | 0.298 | 0.054 | Internal tie-line with 50Hertz
Brunsbuettel - Brunsbuettel - Hamburg/N 952 | 11T0-0000-0025-5 | TENNETGMBH | Brunsbuettel | Brunsbuettel | 400 | [6 empty] | 3600 |  |  | 0.005 | 0.1 | 1.272 | 0.584 | Internal tie-line with 50Hertz
Dillenburg - Dauersberg WO2 | 11T-D2-D7-00020D | TENNETGMBH | Dillenburg | Dauersberg | 400 | [6 empty] | 2612 |  |  | 1.064 | 9.684 | 167.359 | 47.855 | Internal tie-line with Amprion
Hanekenfaehr - Doerpen/W EWBL | 11T-D2-D7-00002F | TENNETGMBH | Doerpen/W | Hanekenfaehr | 400 | [7 empty] | 2216 | 3399 | 1.128 | 10.92 | 164.934 | 32.801 | Internal tie-line with Amprion
Hamburg/S - Dollern 982 | 11T-D2-D8-000051 | TENNETGMBH | Dollern | Hamburg/S | 400 | [6 empty] | 2580 |  |  | 0.45 | 3.535 | 65.201 | 28.687 | Internal tie-line with 50Hertz
Hamburg/S - Dollern 981 | 11T-D2-D8-00063O | TENNETGMBH | Dollern | Hamburg/S | 400 | [6 empty] | 2580 |  |  | 0.45 | 3.535 | 65.201 | 28.687 | Internal tie-line with 50Hertz
Dettingen - Grosskrotzenburg US1 | 11T-D2-D7-00030A | TENNETGMBH | Grosskrotzenburg | Dettingen | 400 | [6 empty] | 2720 |  |  | 0.061 | 0.564 | 9.896 | 4.4 | Internal tie-line with Amprion
Urberach - Grosskrotzenburg UN2 | 11T-D2-D7-000318 | TENNETGMBH | Grosskrotzenburg | Urberach | 400 | [6 empty] | 2720 |  |  | 0.321 | 2.985 | 52.417 | 23.43 | Internal tie-line with Amprion
Hamburg/N - Hamburg/N rot | 11T-D2-D8-000035 | TENNETGMBH | Hamburg/N | Hamburg/N | 220 | [6 empty] | 1647 |  |  | 0.09 | 0.793 | 13.823 | 4.017 | Internal tie-line with 50Hertz
Hamburg/N - Hamburg/N blau | 11TD2L000000319V | TENNETGMBH | Hamburg/N | Hamburg/N | 220 | [6 empty] | 1716 |  |  | 0.077 | 0.845 | 11.498 | 2.926 | Internal tie-line with 50Hertz
Helmstedt - Wolmirstedt 492 | 11T-D2-D8-000213 | TENNETGMBH | Helmstedt | Wolmirstedt | 400 | [6 empty] | 3018 |  |  | 0.755 | 6.805 | 105.642 | 1.792 | Internal tie-line with 50Hertz
Helmstedt - Wolmirstedt 491 | 11T-D2-D8-000205 | TENNETGMBH | Helmstedt | Wolmirstedt | 400 | [6 empty] | 3018 |  |  | 0.755 | 6.805 | 105.642 | 1.799 | Internal tie-line with 50Hertz
Mecklar - Vieselbach 449 | 11T-D2-D8-000302 | TENNETGMBH | Mecklar | Vieselbach | 400 | [6 empty] | 2748 |  |  | 1.775 | 16.325 | 267.108 | 42.624 | Internal tie-line with 50Hertz
Mecklar - Eisenach 450 | 11T-D2-D8-000310 | TENNETGMBH | Mecklar | Eisenach | 400 | [6 empty] | 2748 |  |  | 0.825 | 6.84 | 124.102 | 42.614 | Internal tie-line with 50Hertz
Redwitz - Remptendorf 414 | 11T-D2-D8-00051V | TENNETGMBH | Redwitz | Remptendorf | 400 | [7 empty] | 2619 | 3600 | 0.731 | 7.214 | 126.606 | 37.569 | Internal tie-line with 50Hertz
Redwitz - Remptendorf 413 | 11T-D2-D8-00050X | TENNETGMBH | Redwitz | Remptendorf | 400 | [7 empty] | 2619 | 3600 | 0.79 | 7.463 | 120.386 | 37.585 | Internal tie-line with 50Hertz
Altenfeld - Redwitz 460 | 11T-D2-D8-001015 | TENNETGMBH | Redwitz | Altenfeld | 400 | [6 empty] | 3600 |  |  | 0.472 | 7.084 | 132.855 | 30.952 | Internal tie-line with 50Hertz
Altenfeld - Redwitz 459 | 11T-D2-D8-001007 | TENNETGMBH | Redwitz | Altenfeld | 400 | [6 empty] | 3600 |  |  | 0.472 | 7.084 | 132.855 | 30.955 | Internal tie-line with 50Hertz
Kruemmel - Kruemmel 993 | 11T-D2-D8-00008W | TENNETGMBH | Kruemmel | Kruemmel | 400 | [6 empty] | 3600 |  |  | 0.003 | 0.1 | 0.565 | 0.005 | Internal tie-line with 50Hertz
Kruemmel - Kruemmel 994 | 11T-D2-D8-00009U | TENNETGMBH | Kruemmel | Kruemmel | 400 | [6 empty] | 3600 |  |  | 0.005 | 0.1 | 0.77 | 0.228 | Internal tie-line with 50Hertz
Y-Niederlangen (-Meppen - Doerpen/W) EOWS | 11T0-0000-0983-G | TENNETGMBH | Meppen | Y-Niederlangen | 400 | [6 empty] | 2575 |  |  | 0.257 | 2.96 | 38.485 | 33.278 | Internal tie-line with Amprion
Audorf/S - Hamburg/N weiss | 11T0-0000-0032-A | TENNETGMBH | Hamburg/N | Audorf/S | 400 | [6 empty] | 3600 |  |  | 0.458 | 8.247 | 164.148 | 69.045 | Internal tie-line with 50Hertz
Hamburg/N - Dollern blau | 11T0-0000-0966-F | TENNETGMBH | Hamburg/N | Dollern | 400 | [6 empty] | 3154 |  |  | 0.314 | 5.502 | 97.798 | 43.248 | Internal tie-line with 50Hertz
Meitingen - Oberbachern 419 | 11T-D2-D7-000504 | TENNETGMBH | Meitingen | Oberbachern | 400 | [6 empty] | 2400 |  |  | 0.55 | 6.231 | 112.802 | 49.851 | Internal tie-line with Amprion
Meitingen - Oberbachern 420 | 11T-D2-D7-000512 | TENNETGMBH | Meitingen | Oberbachern | 400 | [6 empty] | 2400 |  |  | 0.55 | 6.231 | 112.802 | 49.851 | Internal tie-line with Amprion
Ohlensehlen - Wehrendorf DS1 | 11T-D2-D7-00004B | TENNETGMBH | Wehrendorf | Ohlensehlen | 400 | [6 empty] | 2616 |  |  | 0.667 | 5.74 | 100.82 | 61.68 | Internal tie-line with Amprion
Nehden - Twistetal TO3 | 11T-D2-D7-00010G | TENNETGMBH | Nehden | Twistetal | 400 | [6 empty] | 2580 |  |  | 0.435 | 4.215 | 74 | 10.976 | Internal tie-line with Amprion
Nehden - Twistetal TW4 | 11T-D2-D7-00011E | TENNETGMBH | Nehden | Twistetal | 400 | [6 empty] | 2580 |  |  | 0.435 | 4.215 | 74 | 10.984 | Internal tie-line with Amprion
Grafenrheinfeld - Hoepfingen 411 | 11T-D2-D4-000014 | TENNETGMBH | Hoepfingen | Grafenrheinfeld | 400 | [6 empty] | 3000 |  |  | 0.961 | 11.877 | 211.115 | 50.132 | Internal tie-line with TNG
Grafenrheinfeld - Stalldorf 416 | 11T-D2-D4-000022 | TENNETGMBH | Stalldorf | Grafenrheinfeld | 400 | [6 empty] | 3000 |  |  | 0.614 | 7.369 | 120.292 | 50.139 | Internal tie-line with TNG
Y-Frankfurt/SW (-Kriftel - Karben) 2 | 11T0-0000-1032-4 | TENNETGMBH | Y-Frankfurt/SW | Kriftel | 400 | [6 empty] | 2760 |  |  | 0.13 | 1.396 | 19.384 | 26.84 | Internal tie-line with Amprion
Guetersloh - Bechterdissen SS1 | 11T-D2-D7-00257J | TENNETGMBH | Guetersloh | Bechterdissen | 400 | [6 empty] | 2720 |  |  | 0.346 | 3.258 | 59.847 | 26.44 | Internal tie-line with Amprion
Altbach - Muehlhausen ws | 11TD400000598-LE | TRANSNETBW | Altbach | Muehlhausen | 400 | [7 empty] | 2544 | 3000 | 0.86 | 8.02 | 140.272 | 31.47
Altbach - Wendlingen bl | 11TD400000597-LI | TRANSNETBW | Altbach | Wendlingen | 400 | [6 empty] | 2000 |  |  | 0.13 | 2.04 | 31.8872 | 7.5
Altlussheim - Daxlanden bl | 11TD400000568-LT | TRANSNETBW | Altlussheim | Daxlanden | 220 | [6 empty] | 2267 |  |  | 1.1557 | 8.713 | 187.02 | 37.8
Altlussheim - GKM bl | 11TD400000580-LE | TRANSNETBW | Altlussheim | GKMB | 220 | [7 empty] | 2505 | 3000 | 0.6281 | 4.6635 | 91.797 | 21.06
Beuren - Gurtweil ge | 11TD400000559-LU | TRANSNETBW | Beuren | Gurtweil | 220 | [6 empty] | 2000 |  |  | 2.32 | 18.52 | 385.034 | 77.4
Beuren - Stockach bl | 11TD400000569-LP | TRANSNETBW | Beuren | Stockach | 220 | [6 empty] | 1980 |  |  | 0.37 | 2.93 | 60.7898 | 12.2
Birkenfeld - Daxlanden ge | 11TD400000581-LA | TRANSNETBW | Birkenfeld | Daxlanden | 220 | [7 empty] | 1123 | 1283 | 0.97 | 6.83 | 141.2146 | 29.3 | Pfinztal
Buehl - Weier gn | 11TD400000566-L0 | TRANSNETBW | Buehl | Weier | 220 | [7 empty] | 1261 | 1595 | 1.6971 | 8.4966 | 111.558 | 28.9
Buenzwangen - Laichingen gn | 11TD400000600-LB | TRANSNETBW | Buenzwangen | Laichingen | 400 | [7 empty] | 2511 | 3000 | 1.09 | 12.41 | 192.1712 | 48.1
Buenzwangen - Wendlingen ge | 11TD400000601-L7 | TRANSNETBW | Buenzwangen | Wendlingen | 400 | [6 empty] | 3000 |  |  | 0.228 | 3.355 | 55.543 | 12.8
Buers - Obermooweiler bl | 11TD400000538-L7 | TRANSNETBW | Buers | Obermooweiler | 400 | [6 empty] | 2052 |  |  | 2.24 | 20.4 | 345.418 | 78.5
Buers - Obermooweiler ws | 11TD400000537-LB | TRANSNETBW | Buers | Obermooweiler | 400 | [6 empty] | 2400 |  |  | 2.28 | 20.5 | 347.146 | 78.5
Daxlanden - Eichstetten gn | 11TD400000588-LJ | TRANSNETBW | Daxlanden | Eichstetten | 400 | [7 empty] | 2352 | 2920 | 3.621 | 31.02 | 542.2389 | 120.7 | Schutter
Daxlanden - Eichstetten rt | 11TD400000577-LS | TRANSNETBW | Daxlanden | Eichstetten | 400 | [7 empty] | 2523 | 3000 | 3.62 | 30.41 | 547.2655 | 120.7 | Oberrhein
Daxlanden - KarlsruheWest ge | 11TD400000590-L9 | TRANSNETBW | Daxlanden | KarlsruheWest | 220 | [6 empty] | 600 |  |  | 0.08 | 0.7 | 11.3726 | 3.5 | Waidfeld
Daxlanden - KarlsruheWest rt | 11TD400000584-LZ | TRANSNETBW | Daxlanden | KarlsruheWest | 220 | [6 empty] | 600 |  |  | 0.08 | 0.7 | 11.3726 | 3.5 | Rappenwört
Daxlanden - Kuehmoos ge | 11T-D4-D7-00004Q | TRANSNETBW | Daxlanden | Kuehmoos | 400 | [6 empty] | 2565 |  |  | 6.064 | 51.62 | 898.4956 | 204.2 | Rheingraben
Daxlanden - Maximiliansau sw | 11T-D4-D7-00002U | TRANSNETBW | Daxlanden | Maximiliansau | 220 | MaximumCurrentImax(A) Period1: 2442; MaximumCurrentImax(A) Period2: 2500 |  |  |  | 0.74785 | 7.8603 | 137.4761 | 5.2 | Period 1: 01.03 -30.10; Period 2 01.11-28.02 German internal tie-line to Amprion, length until x-node
Daxlanden - Oberwald rt | 11TD400000586-LR | TRANSNETBW | Daxlanden | Oberwald | 220 | [7 empty] | 1535 | 1916 | 0.47 | 3.34 | 63.0204 | 13.5 | Seehof
Daxlanden - Philippsburg ge | 11TD400000562-LG | TRANSNETBW | Daxlanden | Philippsburg | 400 | [6 empty] | 3000 |  |  | 0.5859 | 8.71 | 138.23 | 32.6
Daxlanden - Philippsburg rt | 11TD400000585-LV | TRANSNETBW | Daxlanden | Philippsburg | 400 | [6 empty] | 3000 |  |  | 0.586 | 8.712 | 138.135 | 32.7
Daxlanden - RDK7 sw | 11TD400000552-LL | TRANSNETBW | Daxlanden | RDK7 | 400 | [6 empty] | 1200 |  |  | 0.0129 | 0.1507 | 1.7907 | 0.5
Daxlanden - RDK8 gn | 11TD400000547-L6 | TRANSNETBW | Daxlanden | RDK8 | 400 | [7 empty] | 2720 | 3000 | 0.02 | 0.16 | 2.796 | 0.5
Daxlanden - Weingarten ge | 11T-D4-D7-00003S | TRANSNETBW | Daxlanden | Weingarten | 400 | MaximumCurrentImax(A) Period1: 2720; MaximumCurrentImax(A) Period2: 3150 |  |  |  | 0.445 | 4.09 | 71.4084 | 16.4 | German intenral tie-line to Amprion
Dellmensingen - Laichingen ws | 11TD400000526-LK | TRANSNETBW | Dellmensingen | Laichingen | 400 | [7 empty] | 2478 | 2880 | 0.6234 | 6.6472 | 101.0336 | 23.3
Dellmensingen - Obermooweiler gn | 11TD400000535-LJ | TRANSNETBW | Dellmensingen | Obermooweiler | 400 | [7 empty] | 2488 | 2565 | 2.29 | 19.22 | 341.3341 | 76.1
Dellmensingen - Rotensohl bl | 11TD400000593-LY | TRANSNETBW | Dellmensingen | Rotensohl | 400 | [7 empty] | 1800 | 2000 | 1.89 | 18.54 | 276.5858 | 67.1
Dellmensingen - Voehringen gn (Donau W) | 11T-D4-D7-00005O | TRANSNETBW | Dellmensingen | Dellmensingen | 400 | MaximumCurrentImax(A) Period1: 2580; MaximumCurrentImax(A) Period2: 2993 |  |  |  | 0.245 | 2.1 | 36.552 | 16.7 | German internal tie-line to Amprion
Eichstetten - Gurtweil ge | 11TD400000571-LF | TRANSNETBW | Eichstetten | Gurtweil | 220 | [7 empty] | 1092 | 1200 | 4.65 | 22.72 | 256.8566 | 72.3 | Hoellental Ost
Eichstetten - Gurtweil rt | 11TD400000572-LB | TRANSNETBW | Eichstetten | Gurtweil | 220 | [7 empty] | 1092 | 1200 | 4.65 | 22.72 | 256.8566 | 72.3 | Hoellental West
Eichstetten - Kuehmoos gn | 11TD400000560-LO | TRANSNETBW | Eichstetten | Kuehmoos | 400 | [6 empty] | 2400 |  |  | 2.5 | 21.42 | 374.4779 | 83.4 | Dreisam
Eichstetten - Kuehmoos rt | 11TD400000573-L7 | TRANSNETBW | Eichstetten | Kuehmoos | 400 | [7 empty] | 2508 | 3000 | 2.5 | 21.01 | 377.9336 | 83.4 | Kander
Eichstetten - Weier ge | 11TD400000579-LK | TRANSNETBW | Eichstetten | Weier | 220 | [6 empty] | 2500 |  |  | 1.46 | 11.182 | 240.0177 | 48.8
Eichstetten - Weier rt | 11TD400000578-LO | TRANSNETBW | Eichstetten | Weier | 220 | [7 empty] | 1261 | 1496 | 2.88 | 14.35 | 187.773 | 48.8
Endersbach - Wendlingen bl | 11TD400000528-LC | TRANSNETBW | Endersbach | Wendlingen | 400 | [7 empty] | 2509 | 3000 | 0.4992 | 5.213 | 89.881 | 20.3
Engstlatt - Oberjettingen ws | 11T0-0000-0097-8 | TRANSNETBW | Engstlatt | Oberjettingen | 400 | [7 empty] | 2485 | 3000 | 0.85 | 8.96 | 144.7332 | 33.8
Engstlatt - Trossingen rt | 11TD40000A548-L6 | TRANSNETBW | Engstlatt | Trossingen | 400 | [7 empty] | 2720 | 2880 | 0.76 | 9.9 | 159.7814 | 37.3
GKN2 - Grossgartach sw | 11TD400000529-L8 | TRANSNETBW | GKN2 | Grossgartach | 400 | [7 empty] | 2621 | 3000 | 0.47 | 4.35 | 75.8066 | 16.9
Goldshoefe - Rotensohl gn | 11TD400000544-LI | TRANSNETBW | Goldshoefe | Rotensohl | 400 | [6 empty] | 2000 |  |  | 0.52 | 5.44 | 86.5509 | 20.4
Goldshoefe - Kupferzell gn | 11TD400000545-LE | TRANSNETBW | Goldshoefe | Kupferzell | 400 | [7 empty] | 2565 | 3000 | 1.5275 | 13.867 | 249.6624 | 55.2
Grafenrheinfeld - Hoepfingen ge (411) | 11T-D2-D4-000014 | TRANSNETBW | Grafenrheinfeld | Hoepfingen | 400 | [6 empty] | 3000 |  |  | 0.96 | 11.75 | 210.832 | 42.3 | German internal tie-line to TennetG, length until x-node
Grafenrheinfeld - Stalldorf rt (416) | 11T-D2-D4-000022 | TRANSNETBW | Grafenrheinfeld | Stalldorf | 400 | MaximumCurrentImax(A) Period1: 3150; MaximumCurrentImax(A) Period2: 3150 |  |  |  | 0.585 | 6.788 | 123.464 | 4.3 | German internal tie-line to TennetG, length until x-node
Grossgartach - Heilbronn rt | 11TD400000527-LG | TRANSNETBW | Grossgartach | Heilbronn | 400 | [6 empty] | 2000 |  |  | 0.21 | 1.9 | 29.908 | 7
Grossgartach - Hueffenhardt bl | 11TD400000551-LP | TRANSNETBW | Grossgartach | Hueffenhardt | 400 | [7 empty] | 2610 | 3150 | 0.52 | 4.8 | 81.3358 | 18.5
Grossgartach - Kupferzell ws | 11TD400000524-LS | TRANSNETBW | Grossgartach | Kupferzell | 400 | [7 empty] | 2099 | 2583 | 1.25 | 13.66 | 190.1292 | 47.7
Grossgartach - Pulverdingen rt | 11TD40000A530-L6 | TRANSNETBW | Grossgartach 2 | Pulverdingen | 400 | [7 empty] | 2507 | 2880 | 0.757 | 7.8661 | 126.355 | 29.6
Grossgartach - Pulverdingen ws | 11TD400000525-LO | TRANSNETBW | Grossgartach | Pulverdingen | 400 | [7 empty] | 2500 | 2880 | 0.76 | 7.86 | 126.2606 | 29.6
Gruenkraut - Herbertingen rt | 11TD400000534-LN | TRANSNETBW | Gruenkraut | Herbertingen | 400 | [7 empty] | 1722 | 1800 | 1.4 | 12.67 | 153.592 | 41.1
Gruenkraut - Obermooweiler bl | 11TD40000A536-LJ | TRANSNETBW | Gruenkraut | Obermooweiler | 400 | [6 empty] | 1800 |  |  | 0.465 | 4.67 | 82.638 | 18.2
Herbertingen - Tiengen rt | 11T-D4-D7-00010V | TRANSNETBW | Herbertingen | Tiengen | 400 | [6 empty] | 1792 |  |  | 1.975 | 17.82 | 202.475 | 56.565 | German internal tie-line to Amprion, length until x-node
Hoepfingen - Hueffenhardt ge | 11TD400000543-LM | TRANSNETBW | Hoepfingen | Hueffenhardt | 400 | [7 empty] | 2630 | 3000 | 1.36 | 12.11 | 204.2664 | 45.4
Hoheneck - Pulverdingen ws | 11T-D4-D7-00014N | TRANSNETBW | Hoheneck | Pulverdingen | 400 | [6 empty] | 2880 |  |  | 0.135 | 1.735 | 27.2062 | 12.8 | German internal tie-line to Amprion
Karlsruhe Ost - Oberwald rt | 11TD40000A575-L3 | TRANSNETBW | Karlsruhe | Oberwald | 220 | [6 empty] | 651 |  |  | 0.18 | 0.89 | 10.6186 | 2.63
Kuehmoos - Schwoerstadt ge | 11TD400000565-L4 | TRANSNETBW | Kuehmoos | Schwoerstadt | 220 | [7 empty] | 1227 | 1500 | 0.57 | 2.96 | 34.9345 | 9.6
Kuehmoos - Schwoerstadt gn | 11TD400000557-L1 | TRANSNETBW | Kuehmoos | Schwoerstadt | 220 | [7 empty] | 1227 | 1500 | 0.5643 | 2.9349 | 35.6571 | 9.6
Kuehmoos - Tiengen gr | 11T-D4-D7-00012R | TRANSNETBW | Kuehmoos | Tiengen | 220 | [6 empty] | 1290 |  |  | 0.67 | 3.53 | 81.36 | 16.1918 | German internal tie-line to Amprion, length until x-node
Kupferzell - Stalldorf rot | 11TD400000605-LS | TRANSNETBW | Kupferzell | Stalldorf | 400 | [6 empty] | 3000 |  |  | 0.9956 | 11.389 | 217.8695 | 46.8
Marbach - Pulverdingen gn | 11T0-0000-0099-2 | TRANSNETBW | Marbach | Pulverdingen | 220 | [7 empty] | 1274 | 1500 | 0.55 | 4.89 | 74.644 | 17.77
Metzingen - Wendlingen ge | 11TD400000602-L3 | TRANSNETBW | Metzingen | Wendlingen | 400 | [6 empty] | 2000 |  |  | 0.4 | 6.06 | 96.9496 | 22.7
Muehlhausen - Pulverdingen bl | 11TD400000550-LT | TRANSNETBW | Muehlhausen | Pulverdingen | 400 | [7 empty] | 2480 | 2880 | 0.77 | 8 | 134.3973 | 30.7
Neurott - Heidelberg Sued ge | 11TD400000563-LC | TRANSNETBW | Heidelberg | Neurott | 220 | [6 empty] | 542 |  |  | 0.18 | 0.9 | 11.6867 | 3
Neurott - Heidelberg Sued rt | 11TD400000570-LJ | TRANSNETBW | Heidelberg | Neurott | 220 | [6 empty] | 542 |  |  | 0.18 | 0.9 | 11.6867 | 3
Neurott - Philippsburg gn | 11TD400000589-LF | TRANSNETBW | Neurott | Philippsburg | 400 | [6 empty] | 3000 |  |  | 0.44 | 6.123 | 95.158 | 22.17
Neurott - Wiesloch bl | 11TD400000582-L6 | TRANSNETBW | Neurott | Wiesloch | 220 | [6 empty] | 415 |  |  | 0.47 | 2.94 | 35.9712 | 9.6
Oberjettingen - Pulverdingen ws | 11TD400000519-LD | TRANSNETBW | Oberjettingen | Pulverdingen | 400 | [7 empty] | 2486 | 2880 | 1.17 | 12.1 | 194.9673 | 45.6
Y-Bruchsal (- Philippsburg - Pulverdingen) ws | 11T0-0000-1642-7 | TRANSNETBW | Y-Bruchsal | Bruchsal/Kaendelweg | 400 | [6 empty] | 3600 |  |  | 0.1393 | 1.2336 | 24.5358 | 5.2
Y-Bruchsal/Kaendelweg (-Philippsburg - Pulverdingen) rt | 11TD400000521-24 | TRANSNETBW | Y-Bruchsal/Kaendelweg | Bruchsal/Kaendelweg | 400 | [6 empty] | 598 |  |  | 0.14 | 1.24 | 24.693 | 5.2 | tripod - length until Y-Node
Y-Buehl (-Daxlanden - Kuppenheim) rt | 11T0-0000-1478-O | TRANSNETBW | Y-Buehl | Buehl | 220 | [7 empty] | 1262 | 1595 | 1.22 | 6.19 | 82.027 | 21.1 | tripod - length until Y-Node
Y-Daxlanden (-Buehl - Kuppenheim) rt | 11T0-0000-1479-L | TRANSNETBW | Y-Buehl | Daxlanden | 220 | [7 empty] | 2524 | 2567 | 1.16 | 5.71 | 77.4717 | 19.8 | tripod - length until Y-Node
Y-Daxlanden (-Kuppenheim - Weier) ge | 11TD400000574-24 | TRANSNETBW | Daxlanden | Y-Daxlanden | 220 | [7 empty] | 2524 | 2797 | 0.5935 | 4.5624 | 98.1747 | 19.8 | tripod - length until Y-Node
Y-Dellmensingen (-Goldshoefe - Niederstotzingen) ws | 11T0-0000-1365-5 | TRANSNETBW | Y-Dellmensingen | Dellmensingen | 400 | [7 empty] | 1800 | 2404 | 1.09 | 11.49 | 164.2739 | 40.7 | tripod - length until Y-Node
Y-Endersbach (-Grossgartach - Muehlhausen) gn | 11T0-0000-0950-0 | TRANSNETBW | Y-Endersbach | Endersbach | 400 | [6 empty] | 3000 |  |  | 0.45 | 4.26 | 75.0212 | 16.7 | tripod - length until Y-Node
Y-Engstlatt (-Kuehmoos - Villingen) gn | 11TD400000587-1Q | TRANSNETBW | Y-Engstlatt | Engstlatt | 400 | [6 empty] | 2880 |  |  | 1.11 | 14.75 | 236.9704 | 55.4 | tripod - length until Y-Node
Y-Engstlatt (-Oberjettingen - Pulverdingen) rt | 11TD400000520-1A | TRANSNETBW | Engstlatt | Y-Oberjettingen | 400 | [7 empty] | 2487 | 2880 | 0.86 | 9.02 | 145.5814 | 34 | tripod - length until Y-Node
Y-GKM (-Neurott - Weinheim) rt | 11T0-0000-1638-U | TRANSNETBW | GKM | GKMB | 220 | [6 empty] | 2080 |  |  | 0.475 | 3.925 | 77.283 | 15.93 | tripod - length until Y-Node
Y-Goldshoefe (-Dellmensingen - Niederstotzingen) ws | 11T0-0000-1366-2 | TRANSNETBW | Y-Dellmensingen | Goldshoefe | 400 | [7 empty] | 2565 | 3150 | 1.2 | 12.38 | 199.6168 | 46.7 | tripod - length until Y-Node
Y-Grossgartach (-Endersbach - Muelhausen) gn | 11T0-0000-0951-Y | TRANSNETBW | Y-Endersbach | Grossgartach | 400 | [7 empty] | 2720 | 3150 | 0.55 | 5.33 | 170.777 | 27.1 | tripod - length until Y-Node
Y-Gurtweil (-Laufenburg - Stockach) ge-rt | 11T0-0000-1625-6 | TRANSNETBW | Y-Gurtweil | Gurtweil | 220 | [6 empty] | 2080 |  |  | 0.01 | 0.05 | 0.015708 | 0.01 | tripod - length until Y-Node
Y-Herbertingen (-Hoheneck - Metzingen) sw | 11T-D4-D7-00009G | TRANSNETBW | Y-Herbertingen | Herbertingen | 400 | MaximumCurrentImax(A) Period1: 1792; MaximumCurrentImax(A) Period2: 2000 |  |  |  | 0.85 | 16.422 | 276.523 | 61 | tripod - length until Y-Node
Y-Hoheneck (-Herbertingen - Metzingen) sw | 11T0-0000-0963-O | TRANSNETBW | Hoheneck | Y-Hoheneck | 400 | MaximumCurrentImax(A) Period1: 2552; MaximumCurrentImax(A) Period2: 3072 |  |  |  | 0.75 | 7.86 | 137.47 | 62.7 | triüod - length until Y-Node; German internal tie-line to Amprion
Y-Hueffenhardt (-Neurott - Wiesloch) ge | 11TD400000542-1T | TRANSNETBW | Y-Hueffenhardt | Hueffenhardt | 400 | [7 empty] | 2622 | 3150 | 0.9 | 8.08 | 144.796 | 31.8 | tripod - length until Y-Node
Y-Kuehmoos (-Engstlatt - Villingen) gn | 11TD400000587-2O | TRANSNETBW | Y-Engstlatt | Kuehmoos | 400 | [7 empty] | 2578 | 3000 | 1.54 | 17.75 | 321.3535 | 68 | tripod - length until Y-Node
Y-Kuppenheim (-Buehl - Daxlanden) rt | 11T0-0000-1480-7 | TRANSNETBW | Y-Buehl | Kuppenheim | 220 | [6 empty] | 855 |  |  | 0.01 | 0.05 | 0.40841 | 0.1 | tripod - length until Y-Node
Y-Kuppenheim (-Daxlanden - Weier) ge | 11TD400000574-16 | TRANSNETBW | Y-Daxlanden | Kuppenheim | 220 | [6 empty] | 855 |  |  | 0.01 | 0.05 | 0.40841 | 0.1 | tripod - length until Y-Node
Y-Metzingen (-Herbertingen - Hoheneck) sw | 11T-D4-D7-00016J | TRANSNETBW | Y-Herbertingen | Metzingen | 400 | [6 empty] | 3000 |  |  | 0.05 | 0.71 | 11.687 | 2.7 | triüod - length until Y-Node
Y-Muehlhausen (-Endersbach - Grossgartach) gn | 11T0-0000-0952-V | TRANSNETBW | Y-Endersbach | Muehlhausen | 400 | [7 empty] | 2720 | 3150 | 0.24 | 2.43 | 38.4217 | 8.9 | tripod - length until Y-Node
Y-Neurott (-GKM - Weinheim) rt | 11T0-0000-1639-R | TRANSNETBW | GKMB | Neurott | 220 | [7 empty] | 2505 | 2680 | 0.792 | 6.545 | 127.8 | 26.48 | tripod - length until Y-Node
Y-Neurott (-Hueffenhardt - Wiesloch) ge | 11TD400000542-2R | TRANSNETBW | Y-Hueffenhardt | Neurott | 400 | [7 empty] | 2622 | 3000 | 0.2 | 2.06 | 33.3323 | 7.5 | tripod - length until Y-Node
Y-Niederstotzingen (-Dellmensingen - Goldshoefe) ws | 11T0-0000-1368-X | TRANSNETBW | Y-Dellmensingen | Niederstotzingen | 400 | [6 empty] | 556 |  |  | 0.01 | 0.06 | 0.81681 | 0.2 | tripod - length until Y-Node
Y-Oberjettingen (-Engstlatt - Pulverdingen) rt | 11TD400000520-28 | TRANSNETBW | Y-Oberjettingen | Oberjettingen | 400 | [6 empty] | 3120 |  |  | 0.05 | 0.1 | 1.5708 | 0.02 | tripod - length until Y-Node
Y-Philippsburg (-Bruchsal - Pulverdingen) ws | 11T0-0000-1643-4 | TRANSNETBW | Y-Bruchsal | Philippsburg | 400 | [7 empty] | 3006 | 3600 | 0.324 | 4.43 | 68.235 | 16.2 | tripod - length until Y-Node
Y-Philippsburg (-Bruchsal/Kaendelweg - Pulverdingen) rt | 11TD400000521-16 | TRANSNETBW | Y-Bruchsal/Kaendelweg | Philippsburg | 400 | [7 empty] | 2976 | 3600 | 0.32 | 4.41 | 68.267 | 16.3 | tripod - length until Y-Node
Y-Pulverdingen (-Bruchsal - Philippsburg) ws | 11T0-0000-1644-1 | TRANSNETBW | Y-Bruchsal | Pulverdingen | 400 | [6 empty] | 2880 |  |  | 1.0315 | 14.023 | 216.8013 | 51.5 | tripod - length until Y-Node
Y-Pulverdingen (-Bruchsal/Kaendelweg -Philippsburg) rt | 11TD40000A521-36 | TRANSNETBW | Y-Bruchsal/Kaendelweg | Pulverdingen | 400 | [6 empty] | 2880 |  |  | 1.03 | 14.01 | 216.4243 | 51.5 | tripod - length until Y-Node
Y-Pulverdingen (-Engstlatt - Oberjettingen) rt | 11TD400000520-36 | TRANSNETBW | Y-Oberjettingen | Pulverdingen | 400 | [7 empty] | 2483 | 2880 | 1.17 | 12.1 | 194.5903 | 45.6 | tripod - length until Y-Node
Y-Stokach (-Gurtweil - Laufenburg) ge-rt | 11T0-0000-1626-3 | TRANSNETBW | Y-Gurtweil | Stockach | 220 | [6 empty] | 1500 |  |  | 2.1 | 16.8 | 347.3659 | 69.71 | tripod - length until Y-Node
Y-Villingen (-Engstlatt - Kuehmoss) gn | 11TD400000587-3M | TRANSNETBW | Y-Engstlatt | Villingen | 400 | [6 empty] | 478 |  |  | 0.45 | 3.82 | 78.2257 | 16.2 | tripod - length until Y-Node
Y-Weier (-Daxlanden - Kuppenheim) ge | 11TD40000A574-36 | TRANSNETBW | Y-Daxlanden | Weier | 220 | [7 empty] | 2524 | 2797 | 1.4 | 10.75 | 230.6872 | 46.71 | tripod - length until Y-Node
Y-Weinheim (-GKM - Neurott) rt | 11T0-0000-1640-D | TRANSNETBW | GKM | Weinheim | 220 | [7 empty] | 2505 | 3000 | 0.1 | 0.2 | 1.57 | 0.12 | tripod - length until Y-Node
Y-Wiesloch (-Hueffenhardt - Neurott) ge | 11TD400000542-3P | TRANSNETBW | Y-Hueffenhardt | Wiesloch | 400 | [6 empty] | 470 |  |  | 0.06 | 0.56 | 9.8646 | 2.2 | tripod - length until Y-Node

## Tielines
|  |  | Substation_1 | Substation_2 |  | MaximumCurrentImax(A) | [6 empty] | Dynamiclinerating(DLR) |  | Electrical Parameters |  |  | TSO Share until border
NE_name | EIC_Code | TSO | Full_name | Full_name | Voltage_level(kV) | Period1 | Period2 | Period3 | Period4 | Period5 | Period6 | Fixed | DLRmin(A) | DLRmax(A) | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B(μS) | Length_(km) | Comment
Redwitz - Remptendorf 413 | 11T-D2-D8-00050X | 50HERTZ | Redwitz | Remptendorf | 400 | MaximumCurrentImax(A) Period1: 3600 |  |  |  | 0.731 | 7.216 | 126.606 | 18.4 | Tie-line to DE (TTG)
Redwitz - Remptendorf 414 | 11T-D2-D8-00051V | 50HERTZ | Redwitz | Remptendorf | 400 | MaximumCurrentImax(A) Period1: 3600 |  |  |  | 0.731 | 7.216 | 126.606 | 18.4 | Tie-line to DE (TTG)
Röhrsdorf - Hradec 445 | 10T-CZ-DE-00002U | 50HERTZ | Röhrsdorf | Hradec | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.23 | 10.945 | 174.8296 | 51.9 | Tie-line to CZ (CEPS)
Röhrsdorf - Hradec 446 | 10T-CZ-DE-00003S | 50HERTZ | Röhrsdorf | Hradec | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.23 | 10.945 | 174.8296 | 51.9 | Tie-line to CZ (CEPS)
Mecklar - Vieselbach 449-1 | 11T-D2-D8-000302 | 50HERTZ | Mecklar | Vieselbach | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 1.774 | 16.325 | 267.067 | 87.1 | Tie-line to DE (TTG)
Mecklar - Eisenach 450-2 | 11T-D2-D8-000310 | 50HERTZ | Mecklar | Eisenach | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 0.833 | 6.886 | 139.801 | 15.6 | Tie-line to DE (TTG)
Vierraden - Krajnik 507 | 10T-DE-PL-000039 | 50HERTZ | Vierraden | Krajnik | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 0.35 | 3.49 | 57.177 | 13.1 | Tie-line to PL (PSE)
Vierraden - Krajnik 508 | 10T-DE-PL-000047 | 50HERTZ | Vierraden | Krajnik | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 0.35 | 3.49 | 57.177 | 13.1 | Tie-line to PL (PSE)
Hagenwerder - Mikulowa 567 | 10T-DE-PL-00002B | 50HERTZ | Hagenwerder | Mikulowa | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 0.233 | 2.53 | 28.7142 | 2.6 | Tie-line to PL (PSE)
Hagenwerder - Mikulowa 568 | 10T-DE-PL-00001D | 50HERTZ | Hagenwerder | Mikulowa | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 0.243 | 2.606 | 29.8137 | 2.4 | Tie-line to PL (PSE)
Krümmel - Krümmel 993 | 11T-D2-D8-00008W | 50HERTZ | Krümmel | Krümmel | 400 | MaximumCurrentImax(A) Period1: 4000 |  |  |  | 0.004 | 0.2 | 0.031 | 0.2 | Tie-line to DE (TTG)
Krümmel - Krümmel 994 | 11T-D2-D8-00009U | 50HERTZ | Krümmel | Krümmel | 400 | MaximumCurrentImax(A) Period1: 4000 |  |  |  | 0.004 | 0.2 | 0.031 | 0.2 | Tie-line to DE (TTG)
Hamburg/Süd - Dollern 981 | 11T-D2-D8-00063O | 50HERTZ | Hamburg/Süd | Dollern | 400 | MaximumCurrentImax(A) Period1: 2280 |  |  |  | 0.457 | 3.548 | 71 | 28.6 | Tie-line to DE (TTG)
Hamburg/Süd - Dollern 982 | 11T-D2-D8-000051 | 50HERTZ | Hamburg/Süd | Dollern | 400 | MaximumCurrentImax(A) Period1: 2280 |  |  |  | 0.457 | 3.548 | 71 | 28.6 | Tie-line to DE (TTG)
Brunsbüttel - Brunsbüttel 949 | 11T-D2-D8-000027 | 50HERTZ | Brunsbüttel | Brunsbüttel | 400 | MaximumCurrentImax(A) Period1: 2100 |  |  |  | 0.002 | 0.2 | 0.346 | 0.2 | Tie-line to DE (TTG)
Altenfeld - Redwitz 459 | 11T-D2-D8-001007 | 50HERTZ | Altenfeld | Redwitz | 400 | MaximumCurrentImax(A) Period1: 3600 |  |  |  | 0.429 | 7.087 | 132.842 | 25.8 | Tie-line to DE (TTG)
Altenfeld - Redwitz 460 | 11T-D2-D8-001015 | 50HERTZ | Altenfeld | Redwitz | 400 | MaximumCurrentImax(A) Period1: 3600 |  |  |  | 0.94244 | 14.1667 | 265.6845 | 25.8 | Tie-line to DE (TTG)
Helmstedt - Wolmirstedt 491-1 | 11T-D2-D8-000205 | 50HERTZ | Helmstedt | Wolmirstedt | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 0.871 | 6.527 | 104.961 | 46.9 | Tie-line to DE (TTG)
Helmstedt - Wolmirstedt 492-2 | 11T-D2-D8-000213 | 50HERTZ | Helmstedt | Wolmirstedt | 400 | MaximumCurrentImax(A) Period1: 2520 |  |  |  | 0.87 | 6.527 | 104.961 | 46.9 | Tie-line to DE (TTG)
Bauler - Flebour FLE BA N | 10T-LU-DE-00001G | Amprion GmbH | Bauler | Flebour | 220 | [6 empty] | 1290 |  |  | 0.235 | 1.512 | 19.5 | 5.1852 | Tieline Amprion - Creos
Bauler - Flebour FLE BA S | 10T1001C--00096F | Amprion GmbH | Bauler | Flebour | 220 | [6 empty] | 1290 |  |  | 0.235 | 1.512 | 19.5 | 5.1852 | Tieline Amprion - Creos
Beznau - Tiengen AARE O | 10T-CH-DE-000034 | Amprion GmbH | Beznau | Tiengen | 220 | MaximumCurrentImax(A) Period1: 896; MaximumCurrentImax(A) Period2: 896; MaximumCurrentImax(A) Period3: 1093 |  |  |  | 0.245 | 1.91 | 16.2 | 41.932 | Tieline Amprion - Swissgrid
Beznau - Tiengen AARE W | 10T-CH-DE-000026 | Amprion GmbH | Beznau | Tiengen | 400 | MaximumCurrentImax(A) Period1: 1792; MaximumCurrentImax(A) Period2: 1792; MaximumCurrentImax(A) Period3: 2187 |  |  |  | 0.157 | 1.707 | 18.4 | 75.3896 | Tieline Amprion - Swissgrid
Blooren - Trier BLO TR S | 10T-LU-DE-00002E | Amprion GmbH | Trier | Blooren | 220 | [6 empty] | 1290 |  |  | 1.367 | 7.05 | 232.4 | 38.6531 | Tieline Amprion - Creos
Doetinchem - Niederrhein DOETM SW | 10T-DE-NL-00007J | Amprion GmbH | Doetinchem | Niederrhein | 400 | [6 empty] | 3600 |  |  | 0.362 | 7.205 | 153.6 | 31.7676 | Tieline Amprion - Tennet Bv
Doetinchem - Niederrhein DOETM WS | 10T1001C--000235 | Amprion GmbH | Doetinchem | Niederrhein | 400 | [6 empty] | 3600 |  |  | 0.48 | 7.31 | 135 | 29.9983 | Tieline Amprion - Tennet Bv
Ensdorf - St. Avold AVOLD | 10T-DE-FR-00004C | Amprion GmbH | St Avold | Ensdorf | 220 | [6 empty] | 740 |  |  | 0.925 | 4.067 | 47.6 | 13.2865 | Tieline Amprion - RTE
Ensdorf - Vigy VIGY1 N | 10T-DE-FR-00005A | Amprion GmbH | Ensdorf | Vigy | 400 | [6 empty] | 2720 |  |  | 0.365 | 5.13 | 89.2 | 20.4274 | Tieline Amprion - RTE
Ensdorf - Vigy VIGY2 S | 10T-DE-FR-000068 | Amprion GmbH | Ensdorf | Vigy | 400 | [6 empty] | 2720 |  |  | 0.365 | 5.13 | 89.2 | 20.4274 | Tieline Amprion - RTE
Gronau - Hengelo HENGL SW | 10T-DE-NL-00004P | Amprion GmbH | Gronau | Hengelo | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 0.303 | 2.907 | 47.4 | 11.2094 | Tieline Amprion - Tennet Bv
Gronau - Hengelo HENGL WS | 10T-DE-NL-00003R | Amprion GmbH | Gronau | Hengelo | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 0.303 | 2.907 | 47.4 | 11.2094 | Tieline Amprion - Tennet Bv
Heisdorf - Quint HEI QU N | 10T-LU-DE-00003C | Amprion GmbH | Quint | Heisdorf | 220 | [6 empty] | 1290 |  |  | 1.416 | 7.3 | 97.7 | 25.5023 | Tieline Amprion - Creos
Laufenburg - Tiengen ANDLSB | 10T-CH-DE-000131 | Amprion GmbH | Laufenburg | Tiengen | 400 | MaximumCurrentImax(A) Period1: 1620; MaximumCurrentImax(A) Period2: 1792; MaximumCurrentImax(A) Period3: 2140 |  |  |  | 0.403 | 3.599 | 41.8 | 11 | Tieline Amprion - Swissgrid
Leupolz - Westtirol FUESSN O | 10T-AT-DE-10007U | Amprion GmbH | Leupolz | Westtirol | 400 | [6 empty] | 2392 |  |  | 1.219 | 10.69 | 175.3 | 41.3382 | Tieline Amprion - APG
Maasbracht - Oberzier SELFK WS | 10T-DE-NL-00005N | Amprion GmbH | Maasbracht | Oberzier | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2875 |  |  |  | 0.72 | 6.96 | 117.2 | 27.2734 | Tieline Amprion - Tennet Bv
Maasbracht - Siersdorf SELFK SW | 10T-DE-NL-00006L | Amprion GmbH | Maasbracht | Siersdorf | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2875 |  |  |  | 0.495 | 4.935 | 81.6 | 19.1628 | Tieline Amprion - Tennet Bv
Oberzier - Lixhe ALEGRO | 22T201903146---W | Amprion GmbH | Oberzier | Lixhe | 400 | [6 empty] | 3600 |  |  | 0.005 | 0.05 | 0.4 | 0.13505 | Tieline Amprion - Elia
Voehringen - Westtirol FUESSN W | 10T1001C--00037V | Amprion GmbH | Voehringen | Westtirol | 220 | [6 empty] | 1760 |  |  | 2.302 | 19.97 | 339.4 | 79 | Tieline Amprion - APG
Y-Werben (-Buers - Hoheneck - Tiengen) BLUDNZ W | 10T-AT-DE-00025Y | Amprion GmbH | Werben | Y-Werben | 220 | [6 empty] | 1472 |  |  | 0.006 | 0.05 | 0.5 | 0 | Tieline Amprion - APG
Y-Werben (-Buers - Voehringen) DELLM O | 10T-AT-DE-00026W | Amprion GmbH | Werben | Y-Werben | 220 | [6 empty] | 1540 |  |  | 0.01 | 0.059 | 0.4 | 0.1467 | Tieline Amprion - APG
Duernrohr - Slavetice 437 | 10T-AT-CZ-00003X | APG | Duernrohr | Slavetice | 400 | [6 empty] | 2250 |  |  | 1.0335 | 14.265 | 187.3802 | 53.34 | Tieline between AT-CZ
Duernrohr - Slavetice 438 | 10T-AT-CZ-00004V | APG | Duernrohr | Slavetice | 400 | [6 empty] | 2250 |  |  | 1.0335 | 14.265 | 187.3802 | 53.34 | Tieline between AT-CZ
Kainachtal - Maribor 473 | 10T-AT-SI-00001T | APG | Kainachtal | Maribor | 400 | [6 empty] | 1920 |  |  | 0.725 | 9.05 | 105.9973 | 33.7 | Tieline between AT-SI
Kainachtal - Maribor 474 | 10T-AT-SI-00002R | APG | Kainachtal | Maribor | 400 | [6 empty] | 1920 |  |  | 0.725 | 9.05 | 105.9973 | 33.7 | Tieline between AT-SI
Lienz - Soverzene 261 | 10T-AT-IT-00001V | APG | Lienz | Soverzene | 220 | [6 empty] | 704 |  |  | 3.74 | 19.155 | 124.0929 | 33.6 | Tieline between AT-IT
Meiningen - Buers 406A | 10T-AT-DE-000231 | APG | Meiningen | Buers | 220 | [6 empty] | 2040 |  |  | 0.37 | 4.49 | 52.3075 | 28.9 | Tieline between AT-DE
Meiningen - Ruethi 407 | 10T-AT-CH-00003T | APG | Meiningen | Ruethi | 220 | [6 empty] | 2400 |  |  | 0.06 | 0.8 | 8.42 | 2.4 | Tieline between AT-CH
Meiningen - Ruethi 408 | 10T-AT-CH-00004R | APG | Meiningen | Ruethi | 220 | [6 empty] | 2400 |  |  | 0.05 | 0.76 | 8.68 | 2.4 | Tieline between AT-CH
Neusiedl - Gyoer 246B | 10T-AT-HU-00001W | APG | Neusiedl | Gyoer | 220 | [6 empty] | 600 |  |  | 3.325 | 17.105 | 113.7413 | 22.7 | Tieline between AT-HU
Obersielach - Podlog 247 | 10T-AT-SI-00003P | APG | Obersielach | Podlog | 220 | [6 empty] | 920 |  |  | 1.99 | 13.44 | 93.0383 | 19.6 | Tieline between AT-SI
St.Peter - Altheim 233/230 | 10T-AT-DE-00001B | APG | St.Peter | Altheim | 220 | [6 empty] | 1077 |  |  | 0.147 | 0.757 | 5.526 | 1.9 | Tieline between AT-DE
St.Peter - Pirach 256 | 10T-AT-DE-000029 | APG | St.Peter | Pirach | 220 | [6 empty] | 1350 |  |  | 0.134 | 0.698 | 9.364 | 1.9 | Tieline between AT-DE
St.Peter - Pleinting 258 | 10T-AT-DE-000037 | APG | St.Peter | Pleinting | 220 | [6 empty] | 1350 |  |  | 0.134 | 0.698 | 9.364 | 1.9 | Tieline between AT-DE
St.Peter - Simbach 234/230 | 10T-AT-DE-000045 | APG | St.Peter | Simbach | 220 | [6 empty] | 1077 |  |  | 0.147 | 0.757 | 5.526 | 1.9 | Tieline between AT-DE
Walgauwerk - Buers 405A | 10T-AT-DE-10024U | APG | Walgauwerk | Buers | 220 | [6 empty] | 2040 |  |  | 0.185 | 2.24 | 25.9181 | 34.5 | Tieline between AT-DE
Westtirol - Buers 421 | 10T-AT-DE-000061 | APG | Westtirol | Buers | 220 | [6 empty] | 2140 |  |  | 1 | 14.35 | 170.1172 | 92 | Tieline between AT-DE
Westtirol - Buers 422 | 10T-AT-DE-000053 | APG | Westtirol | Buers | 400 | [6 empty] | 2300 |  |  | 0.99 | 14.25 | 168.7035 | 92 | Tieline between AT-DE
Westtirol - Kempten 411 | 10T1001C--00037V | APG | Westtirol | Kempten | 220 | [6 empty] | 1795 |  |  | 1.527 | 12.54 | 210.738 | 47 | Tieline between AT-DE
Westtirol - Leupolz 412 | 10T-AT-DE-10007U | APG | Westtirol | Leupolz | 400 | [6 empty] | 2392 |  |  | 1.33 | 10.65 | 177.9712 | 47 | Tieline between AT-DE
Westtirol - Pradella 427 | 10T-AT-CH-00002V | APG | Westtirol | Pradella | 400 | [6 empty] | 2240 |  |  | 0.835 | 11.4 | 134.8528 | 59.6 | Tieline between AT-CH
Westtirol - Pradella 428 | 10T-AT-CH-00001X | APG | Westtirol | Pradella | 400 | [6 empty] | 2240 |  |  | 0.835 | 11.4 | 134.8528 | 59.6 | Tieline between AT-CH
Wien Suedost - Gyoer 245 | 10T-AT-HU-00002U | APG | Wien Suedost | Gyoer | 220 | [6 empty] | 600 |  |  | 4.992 | 25.665 | 170.7455 | 63.1 | Tieline between AT-HU
Zurndorf - Gyoer 439B | 10T-AT-HU-00003S | APG | Zurndorf | Gyoer | 400 | [6 empty] | 2000 |  |  | 0.19 | 2.79 | 32.5469 | 8.9 | Tieline between AT-HU
Zurndorf - Szombathely 440B | 10T-AT-HU-00004Q | APG | Zurndorf | Szombathely | 400 | [6 empty] | 2000 |  |  | 0.19 | 2.79 | 32.5469 | 8.9 | Tieline between AT-HU
Zaya - Sokolnice 243 | 10T1001C--001215 | APG | Zaya | Sokolnice | 220 | [6 empty] | 800 |  |  | 2.544 | 12.57 | 82.4668 | 13.67 | Tieline between AT-CZ
Zaya - Sokolnice 244 | 10T1001C--001223 | APG | Zaya | Sokolnice | 220 | [6 empty] | 800 |  |  | 2.544 | 12.57 | 82.4668 | 13.67 | Tieline between AT-CZ
Sokolnice - Zaya - V243 | 10T-AT-CZ-000010 | CEPS | Sokolnice | Bisamberg | 220 | [7 empty] | 655 | 900 | 2.55 | 12.57 | 171.5 | 50.8 | Tieline between CZ-AT.
Sokolnice - Zaya - V244 | 10T-AT-CZ-00002Z | CEPS | Sokolnice | Bisamberg | 220 | [7 empty] | 655 | 900 | 2.55 | 12.57 | 171.5 | 50.8 | Tieline between CZ-AT.
Liskovec - Bujakow | 10T-CZ-PL-00002E | CEPS | Liskovec | Bujakow | 220 | [6 empty] | 1050 |  |  | 3.01 | 16.84 | 112 | 23.4 | Tieline between CZ-PL.
Liskovec - Kopanina | 10T-CZ-PL-00003C | CEPS | Liskovec | Kopanina | 220 | [6 empty] | 1050 |  |  | 2.92 | 16.71 | 119 | 23.4 | Tieline between CZ-PL.
Liskovec - P. Bystrica | 10T-CZ-SK-00001Y | CEPS | Liskovec | P. Bystrica | 220 | [7 empty] | 665 | 835 | 3.95 | 19.25 | 120.5 | 61.4 | Tieline between CZ-SK.
Sokolnice - Senice | 10T-CZ-SK-00004S | CEPS | Sokolnice | Senice | 220 | [7 empty] | 755 | 960 | 2.95 | 18.55 | 119.5 | 66.2 | Tieline between CZ-SK.
Nosovice - Varin | 10T-CZ-SK-00002W | CEPS | Nosovice | Varin | 400 | [7 empty] | 1720 | 2000 | 1.06 | 11.95 | 131 | 40.4 | Tieline between CZ-SK.
Sokolnice - Krizovany | 10T-CZ-SK-00003U | CEPS | Sokolnice | Krizovany | 400 | [6 empty] | 2000 |  |  | 1.86 | 19.3 | 246.5 | 54.4 | Tieline between CZ-SK.
Slavetice - Durnrohr - V437 | 10T-AT-CZ-00003X | CEPS | Slavetice | Durnrohr | 400 | [7 empty] | 2250 | 3150 | 1.04 | 14.27 | 187.5 | 42.8 | Tieline between CZ-AT.
Slavetice - Durnrohr - V438 | 10T-AT-CZ-00004V | CEPS | Slavetice | Durnrohr | 400 | [7 empty] | 2250 | 3150 | 1.04 | 14.27 | 187.5 | 42.8 | Tieline between CZ-AT.
Hradec - Etzenricht | 10T-CZ-DE-00001W | CEPS | Hradec | Etzenricht | 400 | [6 empty] | 2000 |  |  | 1.68 | 21.86 | 342.5 | 129.2 | Tieline between CZ-DE.
Prestice - Etzenricht | 10T-CZ-DE-00004Q | CEPS | Prestice | Etzenricht | 400 | [7 empty] | 2265 | 2400 | 1.18 | 14.5 | 225.5 | 75.7 | Tieline between CZ-DE.
Albrechtice - Dobrzen | 10T-CZ-PL-00001G | CEPS | Albrechtice | Dobrzen | 400 | [6 empty] | 2000 |  |  | 2.34 | 24.51 | 297.5 | 24.4 | Tieline between CZ-PL.
Nosovice - Wielopole | 10T-CZ-PL-00004A | CEPS | Nosovice | Wielopole | 400 | [6 empty] | 2000 |  |  | 1.26 | 11.74 | 209 | 38.8 | Tieline between CZ-PL.
Hradec - Rohrsdorf - V445 | 10T-CZ-DE-00002U | CEPS | Hradec | Rohrsdorf | 400 | [7 empty] | 2010 | 2400 | 1.23 | 10.94 | 174.5 | 29.6 | Tieline between CZ-DE.
Hradec - Rohrsdorf - V446 | 10T-CZ-DE-00003S | CEPS | Hradec | Rohrsdorf | 400 | [7 empty] | 2010 | 2400 | 1.23 | 10.94 | 174.5 | 29.6 | Tieline between CZ-DE.
Sokolnice - Stupava | 10T-CZ-SK-00005Q | CEPS | Sokolnice | Stupava | 400 | [6 empty] | 1530 |  |  | 1.3 | 15.74 | 230.5 | 56.6 | Tieline between CZ-SK.
Maribor - Kainachtal | 10T-AT-SI-00001T | ELES | Maribor | Kainachtal | 400 | [6 empty] | 1920 |  |  | 0.718 | 9.0285 | 105.8701 | 28.82 | SI-AT
Maribor - Kainachtal | 10T-AT-SI-00002R | ELES | Maribor | Kainachtal | 400 | [6 empty] | 1920 |  |  | 0.718 | 9.0285 | 105.8701 | 28.82 | SI-AT
Krsko - Tumbri | 10T-HR-SI-00004Z | ELES | Krsko | Tumbri | 400 | [6 empty] | 1920 |  |  | 0.7164 | 7.574 | 87.9351 | 24.07 | SI-HR
Krsko - Tumbri | 10T-HR-SI-00005X | ELES | Krsko | Tumbri | 400 | [6 empty] | 1920 |  |  | 0.7164 | 7.574 | 87.9351 | 24.07 | SI-HR
Divaca - Redipuglia | 10T-IT-SI-000025 | ELES | Divaca | Redipuglia | 400 | [6 empty] | 2688 |  |  | 0.6053 | 7.145 | 96.7501 | 24.35 | SI-IT
Divaca - Melina | 10T-HR-SI-000014 | ELES | Divaca | Melina | 400 | [6 empty] | 1920 |  |  | 1.0205 | 10.863 | 117.734 | 33.24 | SI-HR
Divaca - Pehlin | 10T-HR-SI-000022 | ELES | Divaca | Pehlin | 220 | [6 empty] | 960 |  |  | 1.575 | 11.035 | 74.1098 | 26.61 | SI-HR
Podlog - Obersielach | 10T-AT-SI-00003P | ELES | Podlog | Obersielach | 220 | [6 empty] | 960 |  |  | 1.991 | 13.555 | 78.5561 | 32.75 | SI-AT
Divaca - Padriciano | 10T-IT-SI-000017 | ELES | Divaca | Padriciano | 220 | [6 empty] | 960 |  |  | 0.3405 | 2.389 | 16.0221 | 5.76 | SI-IT
Podlog - Zerjavinec | 10T1001C--001029 | ELES | Podlog | Zerjavinec | 220 | [6 empty] | 780 |  |  | 4.29 | 25.01 | 167.3 | 60.69 | SI-HR
Cirkovce - Zerjavinec | 10T1001C--001037 | ELES | Cikovce | Zerjavinec | 400 | [6 empty] | 1600 |  |  | 2.403 | 17.873 | 221.9371 | 97.8 | SI-HR
Cirkovce - Hevitz | 10T1001C--00101B | ELES | Cirkovce | Hevitz | 400 | [6 empty] | 1600 |  |  | 2.0246 | 22.964 | 288.9506 | 67.8 | SI-HU
MAASBRACHT – VAN EYCK BLACK/27 | 10T-BE-NL-00002G | ELIA | VAN EYCK | MAASBRACHT | 400 | 2448.32 | 2317.16 | 2186 | 2317.16 | 2448.32 |  |  | 2186 | 2570.736 | 0.13657 | 1.5757 | 22.88 | 5.5 | Tie-line to NL (TenneT_NL)
MAASBRACHT – VAN EYCK WHITE/28 | 10T-BE-NL-00001I | ELIA | VAN EYCK | MAASBRACHT | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  | 1999 | 2350.824 | 0.13836 | 1.5778 | 22.9572 | 5.5 | Tie-line to NL (TenneT_NL)
AVELGEM – MASTAING 380.79 | 10T-BE-FR-10004U | ELIA | AVELGEM | MASTAING | 400 | 4380 | 4260 | 4140 | 4260 | 4380 |  |  |  |  | 0.65365 | 11.8041 | 142.6495 | 38.45 | Tie-line to FR (RTE)
AVELGEM – AVELIN 380.80 | 10T-BE-FR-000031 | ELIA | AVELGEM | AVELIN | 400 | 2600.64 | 2461.32 | 2322 | 2461.32 | 2600.64 |  |  | 2322 | 2730.672 | 0.57047 | 6.5764 | 77.3084 | 21.35 | Tie-line to FR (RTE)
RILLAND – ZANDVLIET GREY/29 | 10T-BE-NL-00003E | ELIA | ZANDVLIET | RILLAND | 400 | 2807.84 | 2657.42 | 2507 | 2657.42 | 2807.84 |  |  | 2507 | 2948.232 | 0.17722 | 1.9529 | 15.2205 | 6.95 | Tie-line to NL (TenneT_NL)
RILLAND – ZANDVLIET WHITE/30 | 10T-BE-NL-00004C | ELIA | ZANDVLIET | RILLAND | 400 | 2807.84 | 2657.42 | 2507 | 2657.42 | 2807.84 |  |  | 2507 | 2948.232 | 0.17722 | 1.9529 | 15.2205 | 6.95 | Tie-line to NL (TenneT_NL)
ALEGRO HVDC | 22T201903146---W | ELIA | ALEGRO CONVERTOR STATION | OBERZIER | 400 | 1635 | 1635 | 1635 | 1635 | 1635 |  |  |  |  | 0.0009 | 0.0223 | 7.4456 | 0.1 | HVDC Tie-line to DE (AMPRION)
CHOOZ – MONCEAU 220.48 | 10T-BE-FR-00007U | ELIA | MONCEAU | CHOOZ | 220 | 1184.96 | 1121.48 | 1058 | 1121.48 | 1184.96 |  |  |  |  | 1.6625 | 5.8584 | 38.2394 | 29.4 | Tie-line to FR (RTE)
BELVAL – SOTEL 220.F 2 | 22T20211201P---U | ELIA | BELVAL | SOTEL | 220 | [6 empty] | 9999 |  |  | 0.1 | 0.4 | 1.7 | 1 | Tie-line to LU
Y – SANEM (– AUBANGE – SCHIFFLANGE) 220.512 | 22T201907102---7 | ELIA | REPIQUAGE BIFFERDANGE 220kV | SANEM | 220 | [6 empty] | 1037 |  |  | 0.0881 | 0.30794 | 2.1378 | 1.519 | XB Part Tie-line to LU
Y – AUBANGE (– SCHIFFLANGE – SANEM) 220.512 | 22T201907102---7 | ELIA | AUBANGE | REPIQUAGE BIFFERDANGE 220kV | 220 | [6 empty] | 1050 |  |  | 0.58373 | 4.2367 | 26.1086 | 9.415 | BE Part Tie-line to LU
Y – SCHIFFLANGE (– AUBANGE – SANEM) 220.512 | 22T201907102---7 | ELIA | REPIQUAGE BIFFERDANGE 220kV | SCHIFFLANGE | 220 | [6 empty] | 1312 |  |  | 0.058406 | 0.55411 | 348.1588 | 3.744 | BE Part Tie-line to LU
Y – SCHIFFLANGE (– AUBANGE – SANEM) 220.512 | 22T201907102---7 | ELIA | REPIQUAGE BIFFERDANGE 220kV | SCHIFFLANGE | 220 | [6 empty] | 1312 |  |  | 0.058406 | 0.55411 | 348.1588 | 3.744 | BE Part Tie-line to LU
BELVAL – SOTEL 220.F 1 | 22T20211201Q---P | ELIA | BELVAL | SOTEL | 220 | [6 empty] | 9999 |  |  | 0.1 | 0.4 | 1.7 | 1 | Tie-line to LU
AUBANGE – MOULAINE 220.513 | 10T-BE-FR-000023 | ELIA | AUBANGE | MOULAINE | 220 | 1299.2 | 1229.6 | 1160 | 1229.6 | 1299.2 |  |  | 1160 | 1364.16 | 0.44039 | 3.4752 | 13.714 | 7.85 | Tie-line to FR (RTE)
AUBANGE – MONT-SAINT-MARTIN 220.514 | 10T-BE-FR-00008S | ELIA | AUBANGE | MONT-SAINT-MARTIN | 220 | 1299.2 | 1229.6 | 1160 | 1229.6 | 1299.2 |  |  | 1160 | 1364.16 | 0.10681 | 0.80657 | 6.2636 | 1.935 | Tie-line to FR (RTE)
BELVAL – OXYLUX 220.2 | 22T20211201R---K | ELIA | BELVAL | OXYLUX | 220 | [6 empty] | 1290 |  |  | 0.2178 | 1.1229 | 14.2975 | 1 | Tie-line to LU
SCHIFFLANGE – SCHIFFLANGE 220.1 | 22T20211201S---F | ELIA | SCHIFFLANGE | SCHIFFLANGE | 220 | [6 empty] | 1290 |  |  | 0.05 | 0.2 | 0.85 | 0.5 | Tie-line to LU
ACHENE – LONNY 380.19 | 10T-BE-FR-000015 | ELIA | ACHENE | LONNY | 400 | 2238.88 | 2118.94 | 1999 | 2118.94 | 2238.88 |  |  | 1999 | 2350.824 | 0.78435 | 9.5413 | 94.122 | 31.5 | Tie-line to FR (RTE)
GEZELLE – NEMO CONVERTOR STATION 380.114 | 22T20181019----P | ELIA | GEZELLE | NEMO CONVERTOR STATION | 400 | 1635 | 1635 | 1635 | 1635 | 1635 |  |  |  |  | 0.008003 | 0.011627 | 56.1856 | 0.755 | Internal Line to the HVD convertor station of (Nemo BE-UK HVDC link)
Pecs - Ernestinovo1 491A | 10T-HR-HU-000033 | HOPS | Pecs | Ernestinovo | 400 | [6 empty] | 2001 |  |  | 1.28 | 13.47 | 161.48 | 43.7 | Tie-line to HU (MAVIR)
Pecs - Ernestinovo2 491B | 10T-HR-HU-000041 | HOPS | Pecs | Ernestinovo | 400 | [6 empty] | 2001 |  |  | 1.28 | 13.47 | 161.48 | 43.7 | Tie-line to HU (MAVIR)
Ernestinovo-S. Mitrovica | 10T-RS-HR-00001B | HOPS | Ernestinovo | S. Mitrovica | 400 | [6 empty] | 1920 |  |  | 1.46 | 15.17 | 164.29 | 51.53 | Tie-line to RS (EMS)
Gradacac - Dakovo | 10T-BA-HR-00001V | HOPS | Gradacac | Dakovo | 220 | [6 empty] | 815 |  |  | 1.77 | 9.17 | 60.34 | 27.3 | Tie-line to BA (NOSBiH)
Melina - Divaca | 10T-HR-SI-000014 | HOPS | Melina | Divaca | 400 | [6 empty] | 1920 |  |  | 1.02 | 10.86 | 117.73 | 25.736 | Tie-line to SI (ELES)
Mostar - Konjsko | 10T-BA-HR-00002T | HOPS | Mostar | Konjsko | 400 | [6 empty] | 1920 |  |  | 1.75 | 17.71 | 196.06 | 68.556 | Tie-line to BA (NOSBiH)
Mostar - Zakucac | 10T-BA-HR-00003R | HOPS | Mostar | Zakucac | 220 | [6 empty] | 780 |  |  | 3.79 | 19.79 | 129.7 | 49.463 | Tie-line to BA (NOSBiH)
Pehlin - Divaca | 10T-HR-SI-000022 | HOPS | Pehlin | Divaca | 220 | [6 empty] | 960 |  |  | 1.58 | 11.03 | 74.11 | 24.61 | Tie-line to SI (ELES)
Prijedor - Meduric | 10T-BA-HR-00004P | HOPS | Prijedor | Meduric | 220 | [6 empty] | 780 |  |  | 2.27 | 11.48 | 75.88 | 32.4 | Tie-line to BA (NOSBiH)
Prijedor - Sisak | 10T1001C--00027Y | HOPS | Prijedor | Sisak | 220 | [6 empty] | 780 |  |  | 3.23 | 16.85 | 114.17 | 60.8 | Tie-line to BA (NOSBiH)
Trebinje - Plat 1 | 10T-BA-HR-00019C | HOPS | Trebinje | Plat | 220 | [6 empty] | 675 |  |  | 0.43 | 2.28 | 14.79 | 1.324 | Tie-line to BA (NOSBiH)
Tuzla - Dakovo | 10T-BA-HR-00005N | HOPS | Tuzla | Dakovo | 220 | [6 empty] | 815 |  |  | 3.69 | 18.95 | 124.7 | 26.3 | Tie-line to BA (NOSBiH)
Tumbri - Krsko 1 | 10T-HR-SI-00004Z | HOPS | Tumbri | Krsko | 400 | [6 empty] | 1920 |  |  | 0.72 | 7.57 | 87.94 | 16 | Tie-line to SI (ELES)
Tumbri - Krsko 2 | 10T-HR-SI-00005X | HOPS | Tumbri | Krsko | 400 | [6 empty] | 1920 |  |  | 0.72 | 7.57 | 87.94 | 16 | Tie-line to SI (ELES)
Ugljevik - Ernestinovo | 10T-BA-HR-00006L | HOPS | Ugljevik | Ernestinovo | 400 | [6 empty] | 1920 |  |  | 1.57 | 17.01 | 181.46 | 52.6 | Tie-line to BA (NOSBiH)
Zerjavinec - Podlog | 10T1001C--001029 | HOPS | Zerjavinec | Podlog | 220 | [6 empty] | 780 |  |  | 4.3 | 25.01 | 167.29 | 37.5 | Tie-line to SI (ELES)
Zerjavinec-Cirkovce | 10T1001C--001037 | HOPS | Zerjavinec | Cirkovce | 400 | [6 empty] | 1920 |  |  | 2.75 | 29.05 | 335.87 | 97.8 | Tie-line to SI (ELES)
Zerjavinec-Heviz | 10T-HR-HU-000025 | HOPS | Zerjavinec | Heviz | 400 | [6 empty] | 1920 |  |  | 2.56 | 26.58 | 294.79 | 97.67 | Tie-line to HU (MAVIR)
Arad - Sandorfalva | 10T-HU-RO-000016 | MAVIR | Arad | Sandorfalva | 400 | 1600 | 1600 | 1600 | 1600 | [5 empty] | 1.695 | 17.91 | 183.47 | 53.5 | HU-RO
Gyor - Neusiedl | 10T-AT-HU-00001W | MAVIR | Gyor | Neusiedl | 220 | 600 | 600 | 600 | 600 | [5 empty] | 3.3 | 17.15 | 109.64 | 58.9 | HU-AT
Gyor - Wien | 10T-AT-HU-00002U | MAVIR | Gyor | Wien | 220 | 600 | 600 | 600 | 600 | [5 empty] | 4.955 | 25.63 | 165.25 | 58.9 | HU-AT
Gyor - Zurndorf | 10T-AT-HU-00003S | MAVIR | Gyor | Zurndorf | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 0.744 | 10.44 | 128.18 | 59 | HU-AT
Kisvarda - Mukachevo | 10T-HU-UA-00002F | MAVIR | Kisvarda | Mukachevo | 220 | 820 | 730 | 640 | 730 | [5 empty] | 2.157 | 11.15 | 74.14 | 29.4 | HU-UA
Nadab - Bekescsaba | 10T-HU-RO-000024 | MAVIR | Nadab | Bekescsaba | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 0.898 | 8.91 | 79.8 | 38.81 | HU-RO
Pecs - Ernestinovo1 491A | 10T-HR-HU-000033 | MAVIR | Pecs | Ernestinovo | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.276 | 13.47 | 160.54 | 42.3 | HU-HR
Pecs - Ernestinovo2 491B | 10T-HR-HU-000041 | MAVIR | Pecs | Ernestinovo | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.276 | 13.47 | 160.53 | 42.3 | HU-HR
Sandorfalva - Subotica | 10T-HU-SR-00001A | MAVIR | Sandorfalva | Subotica | 400 | 1600 | 1600 | 1600 | 1600 | [5 empty] | 0.715 | 8.15 | 81.05 | 20.64 | HU-RS
Szabolcsbaka - Mukachevo | 10T1001C--000421 | MAVIR | Szabolcsbaka | Mukachevo | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 0.697 | 7.94 | 102.42 | 27.47 | HU-UA
Szabolcsbaka - Zahidno Ukrainska | 10T1001C--00048Q | MAVIR | Szabolcsbaka | Zahidno Ukrainska | 750 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 2.225 | 34.81 | 420.97 | 19.08 | HU-UA
Szombathely - Zurndorf | 10T-AT-HU-00004Q | MAVIR | Szombathely | Zurndorf | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.769 | 19.46 | 235.31 | 125.9 | HU-AT
Tiszalok - Mukachevo | 10T-HU-UA-00004B | MAVIR | Tiszalok | Mukachevo | 220 | 820 | 730 | 640 | 730 | [5 empty] | 4.845 | 25.3 | 165.88 | 96.7 | HU-UA
Levice - God | 10T-HU-SK-00001T | MAVIR | Levice | God | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.255 | 14.1 | 154.57 | 51 | HU-SK
Gonyu - Velky Dur | 10T1001C--00055T | MAVIR | Gonyu | Velky Dur | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 1.088 | 13.57 | 197.48 | 0.98 | HU-SK
Gonyu - Gabcikovo | 10T1001C--00056R | MAVIR | Gonyu | Gabcikovo | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 0.4 | 4.9 | 70.56 | 0.98 | HU-SK
Sajoivanka - Rimavska Sobota | 10T1001C--00054V | MAVIR | Sajoivanka | Rimavska Sobota | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 0.624 | 7.28 | 95.51 | 23.39 | HU-SK
Gyor - Gabcikovo | 10T-HU-SK-00002R | MAVIR | Gyor | Gabcikovo | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 0.575 | 6.87 | 81.68 | 29.8 | HU-SK
Zerjavinec - Heviz | 10T-HR-HU-000025 | MAVIR | Zerjavinec | Heviz | 400 | 2000 | 2000 | 2000 | 2000 | [5 empty] | 2.523 | 26.21 | 301.28 | 69.9 | HU-HR
Heviz - Cirkovce | 10T1001C--00101B | MAVIR | Heviz | Cirkovce | 400 | 1600 | 1600 | 1600 | 1600 | [5 empty] | 1.337 | 17.737 | 287.2986 | 68.185 | HU-SI
ELK BIS-ALYTUS | 10T-LT-PL-00001B | PSE | ELK BIS | ALYTUS | 400 | 2760 | 2655 | 2550 | 2655 |  |  |  | 2280 | 2970 | 2.144 | 23.216 | 320.8312 | 111.67 | Tie-line to Lithuania (Litgrid)
ELK BIS-ALYTUS | 10T-LT-PL-000029 | PSE | ELK BIS | ALYTUS | 400 | 2760 | 2655 | 2550 | 2655 |  |  |  | 2280 | 2970 | 2.144 | 23.216 | 320.8312 | 111.67 | Tie-line to Lithuania (Litgrid)
KROSNO-LEMESANY | 10T-PL-SK-00002U | PSE | KROSNO | LEMESANY | 400 | 2000 | 2000 | 2000 | 2000 |  |  |  | 2000 | 2000 | 3.57 | 35.34 | 231 | 42.55 | Tie-line to SK (SEPS)
KROSNO-LEMESANY | 10T-PL-SK-00001W | PSE | KROSNO | LEMESANY | 400 | 2000 | 2000 | 2000 | 2000 |  |  |  | 2000 | 2000 | 3.57 | 35.34 | 231 | 42.51 | Tie-line to SK (SEPS)
ZAMOSC-DOBROTWOR | 10T-PL-UA-00001K | PSE | ZAMOSC | DOBROTWOR | 220 | 925.4 | 888.1 | 850.8 | 888.1 |  |  |  | 701.6 | 1000 | 3.5671 | 20.797 | 134.6694 | 62.43 | Tie-line to Ukraine (Ukrenergo)
BUJAKOW-LISKOWIEC | 10T-CZ-PL-00002E | PSE | BUJAKOW | LISKOWIEC | 220 | 1050 | 1050 | 1050 | 1050 |  |  |  | 995 | 1050 | 3.0105 | 16.838 | 112.0041 | 61.977 | Tie-line to CZ (CEPS)
KOPANINA-LISKOWIEC | 10T-CZ-PL-00003C | PSE | KOPANINA | LISKOWIEC | 220 | 1050 | 1050 | 1050 | 1050 |  |  |  | 995 | 1050 | 2.9234 | 17.555 | 118.3678 | 62.213 | Tie-line to CZ (CEPS)
KRAJNIK-VIERRADEN | 10T-DE-PL-000047 | PSE | KRAJNIK | VIERRADEN | 400 | 1500 | 1500 | 1500 | 1500 |  |  |  | 1470.4 | 1500 | 0.352 | 3.888 | 50.5 | 12.85 | Tie-line to DE (50Hz)
KRAJNIK-VIERRADEN | 10T-DE-PL-000039 | PSE | KRAJNIK | VIERRADEN | 400 | 1500 | 1500 | 1500 | 1500 |  |  |  | 1470.4 | 1500 | 0.352 | 3.888 | 50.5 | 12.84 | Tie-line to DE (50Hz)
MIKULOWA-HAGENWERDER | 10T-DE-PL-00001D | PSE | MIKULOWA | HAGENWERDER | 400 | 2380 | 2280 | 2180 | 2280 |  |  |  | 1920 | 2500 | 0.224 | 2.304 | 28.3687 | 11.953 | Tie-line to DE (50Hz)
SLUPSK-STARNO | 10T-PL-SE-000016 | PSE | SLUPSK | STARNO | 400 | 1333 | 1333 | 1333 | 1333 |  |  |  | 1333 | 1333 | 0.016 | 0.048 | 0.0125 | 12.5 | Tile-line to Sweden (SvK)
MIKULOWA-HAGENWERDER | 10T-DE-PL-00002B | PSE | MIKULOWA | HAGENWERDER | 400 | 2380 | 2280 | 2180 | 2280 |  |  |  | 1920 | 2500 | 0.224 | 2.32 | 30.25 | 12.02 | Tie-line to DE (50Hz)
DOBRZEN-ALBRECHTICE | 10T-CZ-PL-00001G | PSE | DOBRZEN | ALBRECHTICE | 400 | 2000 | 2000 | 1900.7 | 2000 |  |  |  | 1610 | 2000 | 2.336 | 24.432 | 298.35 | 132.583 | Tie-line to CZ (CEPS)
WIELOPOLE-NOSOVICE | 10T-CZ-PL-00004A | PSE | WIELOPOLE | NOSOVICE | 400 | 2000 | 2000 | 1900.7 | 2000 |  |  |  | 1610 | 2000 | 1.344 | 12.816 | 160.9 | 48.115 | Tie-line to CZ (CEPS)
LIT 225kV N0 1 AUBANGE - MOULAINE | 10T-BE-FR-000023 | RTE | AUBANGE | MOULAINE | 220 | 1161 | 1230 | 1230 | 1300 | [5 empty] | 0.791 | 6.325 | 42.51 | 15.204 | Tie line to BE (RTE)
LIT 225kV N0 1 AUBANGE - MT-SAINT-MARTIN | 10T-BE-FR-00008S | RTE | AUBANGE | MT-SAINT-MARTIN | 220 | 1161 | 1230 | 1230 | 1300 | [5 empty] | 0.235 | 1.879 | 12.632 | 4.518 | Tie line to BE (RTE)
LIT 225KV N0 1 CAMPOROSSO - MENTO / .CAM | 10T-FR-IT-00004O | RTE | CAMPOROSSO | MENTON/TRINITE VICTOR | 220 | 950 | 1093 | 1093 | 1165 | [5 empty] | 0.73 | 4.42 | 30.834 | 10.893 | Tie line to IT (RTE)
LIT 225kV N0 1 EICHSTETTEN - VOGELGRUN | 10T-DE-FR-00003E | RTE | EICHSTETTEN | VOGELGRUN | 220 | 1100 | 1100 | 1100 | 1283 | [5 empty] | 1.073 | 5.952 | 10.17 | 18.417 | Tie line to DE (RTE)
LIT 225kV N0 1 ENSDORF - ST-AVOLD | 10T-DE-FR-00004C | RTE | ENSDORF | ST-AVOLD | 220 | 740 | 740 | 740 | 740 | [5 empty] | 1.671 | 7.682 | 99.77 | 20.319 | Tie line to DE (RTE)
LIT 225kV N0 1 MONCEAU - CHOOZ | 10T-BE-FR-00007U | RTE | MONCEAU | CHOOZ | 220 | 1057 | 1120 | 1120 | 1184 | [5 empty] | 3.085 | 22.481 | 108.862 | 57.994 | Tie line to BE (RTE)
LIT 400kV N0 1 ACHENE - LONNY | 10T-BE-FR-000015 | RTE | ACHENE | LONNY | 400 | 2000 | 2120 | 2120 | 2240 | [5 empty] | 1.57 | 19.76 | 244 | 64.164 | Tie line to BE (RTE)
LIT 400kV N0 1 AVELGEM - MASTAING | 10T-BE-FR-10004U | RTE | AVELGEM | MASTAING | 400 | 4046 | 4079 | 4079 | 4325 | [5 empty] | 1.885 | 22.003 | 308.932 | 76.148 | Tie line to BE (RTE)
LIT 400kV N0 1 EICHSTETTEN - MUHLBACH | 10T-DE-FR-00002G | RTE | EICHSTETTEN | MUHLBACH | 400 | 2559 | 2559 | 2559 | 2850 | [5 empty] | 0.763 | 8.205 | 70.214 | 31.792 | Tie line to DE (RTE)
LIT 400kV N0 1 ENSDORF - VIGY | 10T-DE-FR-00005A | RTE | ENSDORF | VIGY | 400 | 2720 | 2720 | 2720 | 2720 | [5 empty] | 0.736 | 10.275 | 178.81 | 40.209 | Tie line to DE (RTE)
LIT 400KV N0 1 RONDISSONE - ALBERTVILLE | 10T-FR-IT-00001U | RTE | RONDISSONE | ALBERTVILLE | 400 | 1890 | 1890 | 1890 | 2370 | [5 empty] | 3.028 | 53.581 | 946.954 | 173.27 | Tie line to IT (RTE)
LIT 400KV N0 1 VENAUS - VILLARODIN | 10T-FR-IT-00003Q | RTE | VENAUS | VILLARODIN | 400 | 2585 | 2633 | 2633 | 2715 | [5 empty] | 0.96 | 11.59 | 86.922 | 29.308 | Tie line to IT (RTE)
LIT 400kV N0 2 AVELGEM - AVELIN | 10T-BE-FR-000031 | RTE | AVELGEM | AVELIN | 400 | 4046 | 4194 | 4194 | 4325 | [5 empty] | 1.068 | 13.566 | 154.952 | 19.619 | Tie line to BE (RTE)
LIT 400kV N0 2 ENSDORF - VIGY | 10T-DE-FR-000068 | RTE | ENSDORF | VIGY | 400 | 2720 | 2720 | 2720 | 2720 | [5 empty] | 0.735 | 10.272 | 178.746 | 40.195 | Tie line to DE (RTE)
LIT 400KV N0 2 RONDISSONE - ALBERTVILLE | 10T-FR-IT-00002S | RTE | RONDISSONE | ALBERTVILLE | 400 | 1890 | 1890 | 1890 | 2370 | [5 empty] | 3.029 | 53.551 | 946.98 | 173.233 | Tie line to IT (RTE)
LIT 225 kV BIESCAS-PRAGNERES | 10T-ES-FR-00003X | RTE | BIESCAS | PRAGNERES | 220 | 786 | 857 | 857 | 931 | [5 empty] | 4.426 | 20.387 | 129.296 | 47.93 | Tie line to ES (RTE)
LIT 400 kV HERNANI-ARGIA (BAYONNE SUD) | 10T-ES-FR-00004V | RTE | HERNANI | ARGIA | 400 | 2050 | 2200 | 2200 | 2350 | [5 empty] | 1.519 | 16.847 | 175.612 | 50.643 | Tie line to ES (RTE)
LIT 225 kV ARKALE-ARGIA (BAYONNE SUD) | 10T-ES-FR-000010 | RTE | ARKALE | ARGIA | 220 | 1076 | 1102 | 1102 | 1207 | [5 empty] | 2.25 | 14.301 | 115.97 | 37.14 | Tie line to ES (RTE)
LIT 400 kV VICH-BAIXAS | 10T-ES-FR-00006R | RTE | VICH | BAIXAS | 400 | 2179 | 2237 | 2237 | 2309 | [5 empty] | 3.016 | 32.945 | 422.072 | 106.71 | Tie line to ES (RTE)
Gabcikovo - Gyor | 10T-HU-SK-00002R | SEPS | Gabcikovo | Gyor | 400 | [6 empty] | 2000 |  |  | 0.565 | 6.709 | 58.006 | 13.7 | Tie line with MAVIR
Levice - God | 10T-HU-SK-00001T | SEPS | Levice | God | 400 | [6 empty] | 2000 |  |  | 1.247 | 14.034 | 155.862 | 36.22 | Tie line with MAVIR
V.Dur - Gonyu | 10T1001C--00055T | SEPS | V.Dur | Gonyu | 400 | [6 empty] | 2000 |  |  | 1.111 | 13.231 | 203.533 | 95.5 | Tie line with MAVIR
Gabcikovo - Gonyu | 10T1001C--00056R | SEPS | Gabcikovo | Gonyu | 400 | [6 empty] | 2000 |  |  | 0.388 | 4.621 | 70.537 | 33 | Tie line with MAVIR
R.Sobota - Sajoivanka | 10T1001C--00054V | SEPS | R.Sobota | Sajoivanka | 400 | [6 empty] | 2000 |  |  | 0.694 | 8.072 | 90.029 | 27.8 | Tie line with MAVIR
V.Kapusany - Mukachevo | 10T-SK-UA-00001W | SEPS | V.Kapusany | Mukachevo | 400 | [7 empty] | 1570 | 1980 | 0.829 | 8.703 | 87.8 | 12.44 | Tie line with Ukraenergo
Lemesany - Krosno 1 | 10T-PL-SK-00001W | SEPS | Lemesany | Krosno | 400 | [6 empty] | 2000 |  |  | 1.739 | 17.763 | 255.33 | 79.22 | Tie line with PSE
Lemesany - Krosno 2 | 10T-PL-SK-00002U | SEPS | Lemesany | Krosno | 400 | [6 empty] | 2000 |  |  | 1.735 | 17.752 | 255.33 | 79.22 | Tie line with PSE
Nosovice - Varin | 10T-CZ-SK-00002W | SEPS | Nosovice | Varin | 400 | [7 empty] | 1720 | 2000 | 1.133 | 11.261 | 139.166 | 34.69 | Tie line with CEPS
Krizovany - Sokolnice | 10T-CZ-SK-00003U | SEPS | Krizovany | Sokolnice | 400 | [6 empty] | 2000 |  |  | 1.789 | 19.382 | 234.115 | 71.43 | Tie line with CEPS
Sokolnice - Stupava | 10T-CZ-SK-00005Q | SEPS | Sokolnice | Stupava | 400 | [6 empty] | 2000 |  |  | 1.165 | 14.897 | 210.455 | 54.13 | Tie line with CEPS
Liskovec - P. Bystrica | 10T-CZ-SK-00001Y | SEPS | Liskovec | P. Bystrica | 220 | [7 empty] | 665 | 835 | 4.06 | 20.7 | 124.05 | 33.73 | Tie line with CEPS
Senica - Sokolnice | 10T-CZ-SK-00004S | SEPS | Senica | Sokolnice | 220 | [7 empty] | 785 | 960 | 3.03 | 16.95 | 124.05 | 27.12 | Tie line with CEPS
Arad - Sandorfalva | 10T-HU-RO-000016 | TEL | Arad | Sandorfalva | 400 | [6 empty] | 1920 |  |  | 1.69 | 17.9 | 185.599 | 55 | Tie-line to HU (TEL)
Nadab - Bekescsaba | 10T-HU-RO-000024 | TEL | Nadab | Bekescsaba | 400 | [6 empty] | 2000 |  |  | 0.664 | 5.598 | 86.86 | 20.8 | Tie-line to HU (TEL)
Portile de Fier - Djerdap c1 | 10T-RO-RS-00001V | TEL | Portile de Fier | Djerdap | 400 | [6 empty] | 1920 |  |  | 0.034 | 0.323 | 3.311 | 0.75 | Tie-line to RS (TEL)
Rosiori - Mukacevo c1 | 10T-RO-UA-000010 | TEL | Rosiori | Mukacevo | 400 | [6 empty] | 1920 |  |  | 2.015 | 19.03 | 189.18 | 39 | Tie-line to UA (TEL)
Stupina - Varna c1 | 10T-RO-BG-000038 | TEL | Stupina | Varna | 400 | [6 empty] | 2000 |  |  | 1.474 | 21.559 | 298 | 67.5 | Tie-line to BG (TEL)
Tantareni - Kozlodui c1 | 10T-BG-RO-00001A | TEL | Tantareni | Kozlodui | 400 | [6 empty] | 1920 |  |  | 1.9 | 16.74 | 213.999 | 102 | Tie-line to BG (TEL)
Tantareni - Kozlodui c2 | 10T-RO-BG-00002A | TEL | Tantareni | Kozlodui | 400 | [6 empty] | 1920 |  |  | 1.9 | 16.74 | 213.999 | 102 | Tie-line to BG (TEL)
Rahman - Dobrudja | 10T-RO-BG-00001C | TEL | Dobrudja | Rahman | 400 | [6 empty] | 2000 |  |  | 2.125 | 25.825 | 338.71 | 94.2 | Tie-line to BG (TEL)
Isaccea - Vulcanesti | 30TISAC400VULC-W | TEL | Isaccea | Vulcanesti | 400 | [6 empty] | 1440 |  |  | 0.582 | 8.5675 | 112.4497 | 6.1 | Tie-line to MD (TEL)
Rilland-Zandvliet 380 G | 10T-BE-NL-00003E | TENNET NL | Rilland | Zandvliet | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 0.0945 | 0.9763 | 6.6555 | 6.6 | Tie-line to BE (Elia)
Rilland-Zandvliet 380 W | 10T-BE-NL-00004C | TENNET NL | Rilland | Zandvliet | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 0.0886 | 0.9763 | 6.7361 | 6.6 | Tie-line to BE (Elia)
Maasbracht-Van Eyck 380 W | 10T-BE-NL-00002G | TENNET NL | Maasbracht | Van Eyck | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2875 |  |  |  | 0.1386 | 1.578 | 22.957 | 8.1 | Tie-line to BE (Elia)
Maasbracht-Van Eyck 380 Z | 10T-BE-NL-00001I | TENNET NL | Maasbracht | Van Eyck | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2875 |  |  |  | 0.1364 | 1.5757 | 22.8371 | 8.1 | Tie-line to BE (Elia)
Gronau-Hengelo 380 W | 10T-DE-NL-00003R | TENNET NL | Gronau | Hengelo | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 0.3 | 2.9001 | 45.5214 | 16.4 | Tie-line to DE (Amprion)
Gronau-Hengelo 380 Z | 10T-DE-NL-00004P | TENNET NL | Gronau | Hengelo | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 3100 |  |  |  | 0.3 | 2.9001 | 45.5214 | 16.4 | Tie-line to DE (Amprion)
Maasbracht-Oberzier 380 W | 10T-DE-NL-00005N | TENNET NL | Maasbracht | Oberzier | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2875 |  |  |  | 0.7259 | 7.1484 | 120.4381 | 10.5 | Tie-line to DE (Amprion)
Maasbracht-Siersdorf 380 Z | 10T-DE-NL-00006L | TENNET NL | Maasbracht | Siersdorf | 400 | MaximumCurrentImax(A) Period1: 2500; MaximumCurrentImax(A) Period2: 2875 |  |  |  | 0.4985 | 4.8831 | 81.8009 | 10.5 | Tie-line to DE (Amprion)
Diele-Meeden 380 W | 10T-DE-NL-00002T | TENNET NL | Diele | Meeden | 400 | MaximumCurrentImax(A) Period1: 1520; MaximumCurrentImax(A) Period2: 1520 |  |  |  | 0.3264 | 3.7075 | 52.9723 | 16.5 | Tie-line to DE (TENNET DE)
Diele-Meeden 380 Z | 10T-DE-NL-00001V | TENNET NL | Diele | Meeden | 400 | MaximumCurrentImax(A) Period1: 1520; MaximumCurrentImax(A) Period2: 1520 |  |  |  | 0.3264 | 3.7075 | 52.9723 | 16.5 | Tie-line to DE (TENNET DE)
Doetinchem-Niederrhein 380 W | 10T1001C--000235 | TENNET NL | Doetinchem | Niederrhein | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.4789 | 7.2212 | 131.4207 | 22.18 | Tie-line to DE (Amprion)
Doetinchem-Niederrhein 380 Z | 10T-DE-NL-00007J | TENNET NL | Doetinchem | Niederrhein | 400 | MaximumCurrentImax(A) Period1: 4000; MaximumCurrentImax(A) Period2: 4000 |  |  |  | 0.4708 | 7.1976 | 130.7829 | 22.18 | Tie-line to DE (Amprion)
Etzenricht - Prestice 442 | 10T-CZ-DE-00004Q | TENNETGMBH | Etzenricht | Prestice | 400 | [6 empty] | 2265 |  |  | 1.185 | 14.523 | 244.391 | 33.794 | Tie-line with CEPS
Etzenricht - Hradec 441 | 10T-CZ-DE-00001W | TENNETGMBH | Etzenricht | Hradec | 400 | [6 empty] | 2000 |  |  | 1.772 | 21.705 | 349.04 | 33.786 | Tie-line with CEPS
Handewitt - Kasso 2 | 10T1001C--00064S | TENNETGMBH | Handewitt | Kasso | 400 | [6 empty] | 3349 |  |  | 0.331 | 4.949 | 90.302 | 9.241 | Tie-line with ENDK
Handewitt - Kasso 1 | 10T1001C--00063U | TENNETGMBH | Handewitt | Kasso | 400 | [6 empty] | 3349 |  |  | 0.331 | 4.949 | 90.302 | 9.241 | Tie-line with ENDK
Jardelund - Kasso 1 | 10T-DE-DK-00001I | TENNETGMBH | Jardelund | Kasso | 400 | [6 empty] | 2216 |  |  | 0.296 | 3.466 | 43.668 | 0.971 | Tie-line with ENDK
Jardelund - Kasso 2 | 10T-DE-DK-00002G | TENNETGMBH | Kasso | Jardelund | 400 | [6 empty] | 2216 |  |  | 0.296 | 3.466 | 43.668 | 0.958 | Tie-line with ENDK
Pleinting - St. Peter 258 | 10T-AT-DE-000037 | TENNETGMBH | Pleinting | St. Peter | 220 | [7 empty] | 1360 | 2000 | 2.575 | 13.697 | 180.884 | 46.442 | Tie-line with APG
Westtirol - Silz 413 | 10T1001C--00035Z | TENNETGMBH | Silz | Westtirol | 220 | [6 empty] | 2080 |  |  | 0.085 | 1.14 | 15.523 | 7.831 | Tie-line with APG
Vill - Thaur - Silz 273C | 10T1001C--000332 | TENNETGMBH | Silz | Vill | 220 | [6 empty] | 1572 |  |  | 1.11 | 6.4 | 59.637 | 47.001 | Tie-line with APG
Westtirol - Silz 414 | 10T1001C--00036X | TENNETGMBH | Silz | Westtirol | 220 | [6 empty] | 2080 |  |  | 0.085 | 1.14 | 15.51 | 7.844 | Tie-line with APG
Westtirol - Silz 274E | 10T1001C--000340 | TENNETGMBH | Silz | Westtirol | 220 | [6 empty] | 2080 |  |  | 0.1 | 1.26 | 14.791 | 7.838 | Tie-line with APG
Vill - Thaur - Silz 274C | 10T1001C--000324 | TENNETGMBH | Silz | Vill | 220 | [6 empty] | 1572 |  |  | 1.11 | 6.4 | 59.637 | 47.004 | Tie-line with APG
NordLink cable | 10T-NO-DE-00002J | TENNETGMBH | Wilster/W | Ertsmyra | 400 | [6 empty] | 1095 |  |  | 0.1 | 0.1 | 0 | 623 | Tie-line with Statnett
NordLink cable | 10T-NO-DE-00002J | TENNETGMBH | Wilster/W | Ertsmyra | 400 | [6 empty] | 1095 |  |  | 0.1 | 0.1 | 0 | 623 | Tie-line with Statnett
Diele - Meeden 380 schwarz | 10T-DE-NL-00001V | TENNETGMBH | Meeden | Diele | 400 | [6 empty] | 1520 |  |  | 0.669 | 3.85 | 109.956 | 9.729 | Tie-line with TenneT NL
Diele - Meeden 380 weiss | 10T-DE-NL-00002T | TENNETGMBH | Meeden | Diele | 400 | [6 empty] | 1520 |  |  | 0.669 | 3.85 | 109.956 | 9.722 | Tie-line with TenneT NL
Y-Simbach (-St. Peter - Altheim) 233/230 | 10T1001C--00061Y | TENNETGMBH | St. Peter | Y-Simbach | 220 | [7 empty] | 1102 | 1200 | 0.298 | 2.13 | 15.727 | 7.513 | Tie-line with APG
Pirach - St. Peter 256 | 10T-AT-DE-000029 | TENNETGMBH | St. Peter | Pirach | 220 | [7 empty] | 1360 | 2000 | 2.215 | 11.829 | 155.368 | 40.2375 | Tie-line with APG
Y-Simbach (-St. Peter - Altheim) 234/230 | 10T1001C--00062W | TENNETGMBH | St. Peter | Y-Simbach | 220 | [6 empty] | 1200 |  |  | 0.298 | 2.13 | 15.727 | 7.513 | Tie-line with APG
Asphard - Kuehmoos rt (Wehra) | 10T-CH-DE-000018 | TRANSNETBW | Asphard | Kuehmoos | 400 | 1920 | 2352 | 2530 | 2530 | [5 empty] | 0.39 | 3.56 | 60.0987 | 26.4 | Tieline between DE-CH
Buers - Meiningen gn (406A) | 10T-AT-DE-000231 | TRANSNETBW | Buers | Meiningen | 220 | [6 empty] | 2040 |  |  | 0.37 | 4.485 | 52.4018 | 28.9 | Tieline between DE-AT
Buers - Walgau or (405A) | 10T-AT-DE-10024U | TRANSNETBW | Buers | Walgau | 220 | [6 empty] | 2040 |  |  | 0.185 | 2.24 | 25.9181 | 14.35 | Tieline between DE-AT
Buers - Westtirol rt (422) | 10T-AT-DE-000053 | TRANSNETBW | Buers | Westtirol | 400 | [6 empty] | 1965 |  |  | 0.99 | 14.27 | 168.7035 | 91.4 | Tieline between DE-AT
Buers - Westtirol ws (421) | 10T-AT-DE-000061 | TRANSNETBW | Buers | Westtirol | 220 | [6 empty] | 2154 |  |  | 1 | 14.365 | 170.1173 | 92 | Tieline between DE-AT
Buers - Y-Werben | 11T-D4-D7-00001W | TRANSNETBW | Buers | Y-Werben | 220 | [6 empty] | 1710 |  |  | 0.595 | 90.8 | 70.4188 | 47 | Tieline between DE-FR
Eichstetten - Muhlbach rt (Ill) | 10T-DE-FR-00002G | TRANSNETBW | Eichstetten | Muhlbach | 400 | MaximumCurrentImax(A) Period1: 2559; MaximumCurrentImax(A) Period2: 3000 |  |  |  | 0.38 | 4.1 | 70.3403 | 17.38 | Tieline between DE-FR
Eichstetten - Vogelgrun ge (Kaiserstuhl) | 10T-DE-FR-00003E | TRANSNETBW | Eichstetten | Vogelgrun | 220 | MaximumCurrentImax(A) Period1: 1100; MaximumCurrentImax(A) Period2: 1302 |  |  |  | 0.535 | 2.975 | 32.5155 | 17.01 | Tieline between DE-CH
Gurtweil - Oftringen bl | 10T1001C--000227 | TRANSNETBW | Gurtweil | Oftringen | 220 | MaximumCurrentImax(A) Period1: 960; MaximumCurrentImax(A) Period2: 1265; MaximumCurrentImax(A) Period3: 1176 |  |  |  | 1.285 | 9.13 | 141.9686 | 22.18 | Tieline between DE-CH
Kuehmoos - Laufenburg br (Heimbach) | 10T-CH-DE-00008V | TRANSNETBW | Kuehmoos | Laufenburg | 400 | MaximumCurrentImax(A) Period1: 1920; MaximumCurrentImax(A) Period2: 2400; MaximumCurrentImax(A) Period3: 2352 |  |  |  | 0.13 | 1.1 | 20.169 | 8.23 | Tieline between DE-CH
Kuehmoos - Laufenburg ge (Seelbach) | 10T-CH-DE-00009T | TRANSNETBW | Kuehmoos | Laufenburg | 400 | MaximumCurrentImax(A) Period1: 1920; MaximumCurrentImax(A) Period2: 2400; MaximumCurrentImax(A) Period3: 2352 |  |  |  | 0.13 | 1.105 | 19.2265 | 4 | Tieline between DE-CH
Kuehmoos - Laufenburg rt (Murg) | 10T-CH-DE-000107 | TRANSNETBW | Kuehmoos | Laufenburg | 400 | MaximumCurrentImax(A) Period1: 1920; MaximumCurrentImax(A) Period2: 2138; MaximumCurrentImax(A) Period3: 2138 |  |  |  | 0.14 | 1.13 | 20.0277 | 8.1 | Tieline between DE-CH
Kuehmoos - Laufenburg ws (Hotzenwald) | 10T-CH-DE-000123 | TRANSNETBW | Kuehmoos | Laufenburg | 220 | MaximumCurrentImax(A) Period1: 1130; MaximumCurrentImax(A) Period2: 1418; MaximumCurrentImax(A) Period3: 1130 |  |  |  | 0.285 | 1.465 | 26.0752 | 8.58 | Tieline between DE-CH
Laufenburg - Trossingen rt | 10T-CH-DE-000050 | TRANSNETBW | Laufenburg | Trossingen | 400 | MaximumCurrentImax(A) Period1: 1920; MaximumCurrentImax(A) Period2: 2400; MaximumCurrentImax(A) Period3: 2352 |  |  |  | 0.89 | 10.735 | 181.8982 | 81.5 | Tieline between DE-CH
Y-Kuehmoos (-Laufenburg - Lindenholz) bl | 10T-CH-DE-000115 | TRANSNETBW | Kuehmoos | Y-Kuehmoos | 220 | MaximumCurrentImax(A) Period1: 900; MaximumCurrentImax(A) Period2: 1190; MaximumCurrentImax(A) Period3: 1102 |  |  |  | 0.325 | 1.685 | 19.9491 | 10.24 | Tieline between DE-CH
Y-Laufenburg (-Gurtweil - Stokach) rtge | 11T0-0000-1627-0 | TRANSNETBW | Gurtweil | Y-Laufenburg | 220 | MaximumCurrentImax(A) Period1: 1200; MaximumCurrentImax(A) Period2: 1500; MaximumCurrentImax(A) Period3: 1236 |  |  |  | 0.45 | 3.1 | 57.8681 | 21.88 | Tieline between DE-CH

## Transformers
Location |  |  | Maximum Current Imax (A) primary |  |  | Voltage_level(kV) |  | Electrical Parameters (primary) at neutral tap |  |  |  | Phase Shifting Properties
Full Name | EIC_Code | TSO | Min | Max | Fixed | Primary | Secondary | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B (µS) | Conductance_G (µS) | Taps used for RAO | Theta θ (°) | Symmetrical/Asymmetrical | Phase Regulation δu (%) | Angle Regulation δu (%) | Comment
TR Eula 220/400 401 | 11TD8T401EU12--E | 50HERTZ | 866 | 866 |  | 400 | 231 | 0.66759 | 51.4623 | -415.27 | 2.5618 |  |  |  | 1.385 | 0
TR Güstrow 220/400 403 | 11TD8T403GUE12-P | 50HERTZ | 1215 | 1215 |  | 380 | 231 | 0.36128 | 22.9947 | -477.407 | 3.1903 |  |  |  | 1.273 | 0
TR Hamburg/Nord 220/400 405 | 11TD8T405NOR12-5 | 50HERTZ | 650 | 650 |  | 400 | 231 | 0.92544 | 62.9265 | -437.567 | 2.0577 |  |  |  | 1.231 | 0
TR Hamburg/Nord 220/400 406 | 11TD8T406NOR12-Y | 50HERTZ | 650 | 650 |  | 400 | 231 | 0.92544 | 62.9265 | -0.5687 | 0.7688 |  |  |  | 1.231 | 0
TR Lubmin 220/400 405 | 11T0-0000-0003-J | 50HERTZ | 650 | 650 |  | 400 | 231 | 0.7375 | 67.022 | -0.54673 | 0.75 |  |  |  | 1.231 | 0
TR Marzahn 220/400 401 | 11TD8T401MZA12-Q | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.50591 | 40.4288 | -1.1255 | 0.5437 |  |  |  | 1.231 | 0
TR Marzahn 220/400 402 | 11TD8T402MZA12-I | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.50591 | 40.4288 | -1.1255 | 0.5437 |  |  |  | 1.231 | 0
TR Neuenhagen 220/400 401 | 11TD8T401NHG12-N | 50HERTZ | 958 | 958 |  | 380 | 231 | 0.41864 | 23.9487 | -669.555 | 3.8574 |  | -60 | Asymmetrical |  | 1.182
TR Neuenhagen 220/400 402 | 11TD8T402NHG12-F | 50HERTZ | 958 | 958 |  | 380 | 231 | 0.41864 | 23.9487 | -477.155 | 3.1245 |  | -60 | Asymmetrical |  | 1.182
TR Remptendorf 220/400 401 | 11TD8T401RE12--J | 50HERTZ | 577 | 577 |  | 380 | 231 | 0.91711 | 63.1933 | -0.75 | 1 |  |  |  | 1.231 | 0
TR Remptendorf 220/400 402 | 11TD8T402RE12--B | 50HERTZ | 577 | 577 |  | 380 | 231 | 0.91711 | 63.1933 | -0.75 | 1 |  |  |  | 1.231 | 0
TR Röhrsdorf 220/400 402 | 11TD8T402ROE12-T | 50HERTZ | 1215 | 1215 |  | 380 | 231 | 0.33283 | 22.5167 | -477.407 | 3.1252 |  |  |  | 1.273 | 0
TR Röhrsdorf 220/400 403 | 11TD8T403ROE12-T | 50HERTZ | 1215 | 1215 |  | 380 | 231 | 0.33283 | 22.5167 | -477.407 | 3.1252 |  |  |  | 1.273 | 0
PST Röhrsdorf 441 | 11T0-0000-0011-L | 50HERTZ | 2028 | 2028 |  | 410 | 410 | 0.1 | 12.607 | -0.90226 | 1.1065 | -10;10 | 90 | Symmetrical |  | 1.069 | Can be connected to different (non cross-border) lines
PST Röhrsdorf 442 | 11T0-0000-0012-I | 50HERTZ | 2028 | 2028 |  | 410 | 410 | 0.097 | 17.02 | -0.15862 | 0.696 | -10;10 | 90 | Symmetrical |  | 1.069 | Can be connected to different (non cross-border) lines
TR Thyrow 220/400 401 | 11TD8T401THY12-2 | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.91711 | 63.1933 | -0.75 | 1 |  |  |  | 1.231 | 0
PST Vierraden 441 | 11T0-0000-0013-F | 50HERTZ | 2028 | 2028 |  | 410 | 410 | 0.1 | 16.754 | -0.90226 | 1.1065 | -10;10 | 90 | Symmetrical |  | 1.069 | Either connected to 10T-DE-PL-000039 or 10T-DE-PL-000047 (only one line active)
PST Vierraden 443 | 11T0-0000-0014-C | 50HERTZ | 2028 | 2028 |  | 410 | 410 | 0.097 | 17.02 | -0.15862 | 0.696 | -10;10 | 90 | Symmetrical |  | 1.069 | Either connected to 10T-DE-PL-000039 or 10T-DE-PL-000047 (only one line active)
TR Vierraden 220/400 402 | 11T0-0000-0026-2 | 50HERTZ | 650 | 650 |  | 400 | 231 | 0.7375 | 67.022 | -0.56872 | 0.7688 |  |  |  | 1.231 | 0
TR Vierraden 220/400 404 | 11T0-0000-0028-X | 50HERTZ | 650 | 650 |  | 400 | 231 | 0.7375 | 67.022 | -0.56872 | 0.7688 |  |  |  | 1.231 | 0
TR Vieselbach 220/400 402 | 11TD8T402VIB12-B | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.91711 | 63.1933 | -0.75 | 1 |  |  |  | 1.231 | 0
TR Vieselbach 220/400 403 | 11TD8T403VIB12-B | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.91711 | 63.1933 | -0.75 | 1 |  |  |  | 1.231 | 0
TR Wolmirstedt 220/400 403 | 11TD8T403WOL12-P | 50HERTZ | 1215 | 1215 |  | 380 | 231 | 0.3518 | 22.8342 | -346.131 | 2.747 |  |  |  | 1.273 | 0
TR Wolmirstedt 220/400 404 | 11TD8T404WOL12-H | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.91711 | 63.1933 | -0.75 | 1 |  |  |  | 1.231 | 0
TR Wustermark 220/400 401 | 11TD8T401WU12-0Y | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.9274 | 62.578 | -0.67082 | 0.775 |  |  |  | 1.231 | 0
TR Wustermark 220/400 402 | 11TD8T402WU12--S | 50HERTZ | 577 | 577 |  | 400 | 231 | 0.91711 | 63.1933 | -0.75 | 1 |  |  |  | 1.231 | 0
TR Brauweiler | 11T0-0000-1249-6 | Amprion GmbH |  | 2008 |  | 230 | 400 | 0.176 | 16.046 | -3.6 | 4.3 |  |  |  | 1.231
TR Buerstadt | 11T0-0000-0572-6 | Amprion GmbH |  | 2008 |  | 230 | 400 | 0.247 | 16.838 | -45 | 6 |  |  |  | 1.231
TR Buerstadt | 11T0-0000-0571-9 | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | -60 |  |  | 1.385
TR Buescherhof | 11T0-0000-0575-Y | Amprion GmbH |  | 1924 |  | 240 | 400 | 0.226 | 17.76 | -16.3 | 5.5 |  |  |  | 1.231
TR Dauersberg | 11T0-0000-1251-Q | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.232 | 23.806 | -3 | 0.9 |  | 60 |  |  | 1.389
TR Dauersberg | 11T0-0000-0589-I | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | 60 |  |  | 1.385
TR Eiberg | 11T0-0000-0595-Q | Amprion GmbH |  | 1924 |  | 240 | 400 | 0.24 | 17.278 | -6.4 | 5.3 |  |  |  | 1.231
TR Ensdorf | 11T0-0000-0263-M | Amprion GmbH |  | 2008 |  | 230 | 230 | 0.089 | 10 | -3.7 | 1.1 |  | 90 | SYMM |  | 2.6
TR Ensdorf | 11T0-0000-0606-H | Amprion GmbH |  | 2008 |  | 230 | 400 | 0.176 | 16.046 | -3.6 | 4.3 |  |  |  | 1.231
TR Gersteinwerk | 11T0-0000-0614-J | Amprion GmbH |  | 2008 |  | 230 | 400 | 0.235 | 16.738 | -5.4 | 3 |  |  |  | 1.231
TR Gersteinwerk | 11T0-0000-0615-G | Amprion GmbH |  | 2008 |  | 230 | 400 | 0.117 | 15.784 | -5.4 | 1.6 |  |  |  | 1.231
PST Gronau | 11T0-0000-0620-R | Amprion GmbH |  | 2165 |  | 400 | 400 | 0.131 | 3.31 | -6.2 | 2.9 | -10;10 | 90 | ASYM | 1.283 | 1.111 | PST connected to substation Gronau.
TR Hanekenfaehr | 11T0-0000-1278-Y | Amprion GmbH |  | 2008 |  | 230 | 400 | 0.229 | 16.483 | -11 | 5.2 |  |  |  | 1.231
TR Hattingen | 11T0-0000-0646-1 | Amprion GmbH |  | 2008 |  | 230 | 400 | 0.235 | 16.662 | -37.3 | 3.4 |  |  |  | 1.257
TR Hoheneck | 11T0-0000-0650-F | Amprion GmbH |  | 1271 |  | 400 | 231 | 0.558 | 25.68 | -7.6 | 1.7 |  | 60 |  |  | 1.385
TR Kusenhorst | 11T0-0000-0683-V | Amprion GmbH |  | 2008 |  | 230 | 400 | 0.206 | 16.221 | -17.2 | 5.7 |  |  |  | 1.231
TR Niederrhein | 11T0-0000-0754-Z | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | 60 |  |  | 1.385
TR Niederstedem | 11T0-0000-0759-K | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | -60 |  |  | 1.385
TR Niederstedem | 11T0-0000-0758-N | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | -60 |  |  | 1.385
TR Niederstedem | 11T0-0000-0760-6 | Amprion GmbH |  | 1155 |  | 400 | 231 | 0.459 | 45.176 | -1.6 | 0.5 |  | -60 |  |  | 0.689
TR Opladen | 11T0-0000-0796-D | Amprion GmbH |  | 1924 |  | 240 | 400 | 0.24 | 17.276 | -39.1 | 6.1 |  |  |  | 1.231
TR Opladen | 11T0-0000-1674-Q | Amprion GmbH |  | 2008 |  | 230 | 400 | 0.176 | 16.046 | -3.6 | 4.3 |  |  |  | 1.231
TR St. Peter | 11T0-0000-0858-I | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | 60 |  |  | 1.385
TR St. Peter | 11T0-0000-1348-4 | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | 60 |  |  | 1.385
TR Rommerskirchen | 11T0-0000-0833-4 | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | 60 |  |  | 1.385
TR Sechtem | 11T0-0000-0847-P | Amprion GmbH |  | 1795 |  | 230 | 400 | 0.176 | 16.046 | -3.6 | 4.3 |  |  |  | 1.231
TR Tiengen | 11T0-0000-0859-F | Amprion GmbH |  | 1271 |  | 400 | 231 | 0.446 | 24.741 | -1 | 1.6 |  | -60 |  |  | 1.385
TR Uchtelfangen | 11T0-0000-0862-W | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | -60 |  |  | 1.385
TR Urberach | 11T0-0000-0874-M | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | -60 |  |  | 1.385
TR Urberach | 11T0-0000-0875-J | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | -60 |  |  | 1.385
TR Utfort | 11T0-0000-0879-7 | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | 60 |  |  | 1.385
TR Utfort | 11T0-0000-0878-A | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | 60 |  |  | 1.385
TR Voehringen | 11T0-0000-0884-I | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.232 | 23.806 | -3 | 0.9 |  | -60 |  |  | 1.389
TR Walsum | 11T0-0000-1352-I | Amprion GmbH |  | 2008 |  | 230 | 400 | 0.176 | 16.046 | -3.6 | 4.3 |  |  |  | 1.231
TR Wehrendorf | 11T0-0000-0893-H | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | 60 |  |  | 1.385
TR Westerkappeln | 11T0-0000-0914-4 | Amprion GmbH |  | 2008 |  | 230 | 400 | 0.229 | 16.482 | -28 | 4.6 |  |  |  | 1.231
TR Weissenthurm | 11T0-0000-0904-8 | Amprion GmbH |  | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 |  | 60 |  |  | 1.385
TR Duernrohr DURHU41 | 14T-38220-DR0410 | APG |  |  | 1556 | 220 | 400 | 0.2196 | 15.786 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
TR Duernrohr DURHU42 | 14T-38220-DR042Z | APG |  |  | 1556 | 220 | 400 | 0.2196 | 15.786 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
TR Ernsthofen EHRHU41 | 14T-38220-EH0425 | APG |  |  | 1556 | 220 | 400 | 0.2196 | 15.873 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
TR Ernsthofen EHRHU42 | 14T-38220-EH0417 | APG |  |  | 1556 | 220 | 400 | 0.2196 | 15.786 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
PST Ernsthofen EHPST | 14T-22220-EHPST5 | APG |  |  | 1493 | 220 | 220 | 0.1223 | 12.827 | 63.1514 | 1.6833 | -6; +6 | 90 | SYMM |  | 2.252 | PST connected to substation Ernsthofen
TR Lienz LIRHU41 | 14T-38220-LI041Y | APG |  |  | 1554 | 220 | 400 | 0.2196 | 15.433 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
TR Lienz LIRHU42 | 14T-38220-LI042W | APG |  |  | 1554 | 220 | 400 | 0.2196 | 15.433 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
PST Lienz LIPST | 14T-22220-LIPSTW | APG |  |  | 746 | 220 | 220 | 0.2937 | 23.591 | 4.3939 | 1.7895 |  | 90 | SYMM |  | 3.616 | PST coordinated in Italy North; PST connected to substation Lienz
TR Obersielach OSRHU41 | 14T-38220-OS0413 | APG |  |  | 1556 | 220 | 400 | 0.2196 | 15.433 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
TR Obersielach OSRHU43 | 14T-RHU43-OS---K | APG |  |  | 1531 | 220 | 400 | 0.1773 | 15.609 | -10.0555 | 2.6427 |  | 60 | ASYM |  | 1.253
TR Obersielach OSRHU42 | 14T-38220-OS0421 | APG |  |  | 1556 | 220 | 400 | 0.2196 | 15.433 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
TR St. Peter SPRHU41 | 14T-38220-SP041V | APG |  |  | 1427 | 220 | 400 | 0.1942 | 15.099 | -6.7194 | 2.7958 |  | -60 | ASYM |  | 1.253
TR St. Peter SPRHU42 | 14T-38220-SP042T | APG |  |  | 1427 | 220 | 400 | 0.1942 | 15.099 | -6.7194 | 2.7958 |  | -60 | ASYM |  | 1.253
TR St. Peter SPRHU43 | 14T-38220-SP043R | APG |  |  | 1427 | 220 | 400 | 0.1942 | 15.099 | -6.7194 | 2.7958 |  | -60 | ASYM |  | 1.253
TR Tauern TARHU41 | 14T-38220-TA041Q | APG |  |  | 1554 | 220 | 400 | 0.1925 | 15.432 | -12.6401 | 5.0472 |  | 60 | ASYM |  | 1.253
TR Tauern TARHU42 | 14T-38220-TA042O | APG |  |  | 1554 | 220 | 400 | 0.1925 | 15.432 | -12.6401 | 5.0472 |  | 60 | ASYM |  | 1.253
PST Tauern TAPST | 14T-22220-TAPSTO | APG |  |  | 1493 | 220 | 220 | 0.1223 | 12.827 | 63.1514 | 1.6833 | -6; +6 | 90 | SYMM |  | 2.252 | PST connected to substation Tauern
PST Ternitz TEPST | 14T-22220-TEPST4 | APG |  |  | 1493 | 220 | 220 | 0.1223 | 12.827 | 63.1514 | 1.6833 | -6; +6 | 90 | SYMM |  | 2.252 | PST connected to substation Ternitz
TR Westtirol WTRHU41 | 14T-38220-WT041O | APG |  |  | 1443 | 400 | 220 | 0.2987 | 21.601 | -6.6615 | 1.7 |  | 59.99 | ASYM |  | 1.388
TR Wien Suedost SORHU41 | 14T-38221-SO041S | APG |  |  | 1556 | 220 | 400 | 0.2196 | 15.786 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
TR Wien Suedost SORHU43 | 14T-38220-SO042Y | APG |  |  | 1556 | 220 | 400 | 0.2196 | 15.786 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
TR Zell am Ziller ZZRHU41 | 14T-38220-ZZ041D | APG |  |  | 1732 | 400 | 220 | 0.2257 | 19.736 | -22.4514 | 1.0437 |  | 59.95 | ASYM |  | 1.25
TR Zell am Ziller ZZRHU42 | 14T-38220-ZZ042B | APG |  |  | 1732 | 400 | 220 | 0.2257 | 19.736 | -22.4514 | 1.0437 |  | 59.95 | ASYM |  | 1.25
TR Zaya ZYRHU41 |  | APG |  |  | 1427 | 220 | 400 | 0.17738 | 15.609 | -10.0555 | 2.6427 |  | 60 | ASYM |  | 1.253 | No EIC code yet, as only recently put into operation
TR C. Stred T401 | 27T-TR-CSTT401-T | CEPS |  |  | 722 | 400 | 231 | 0.42 | 39.84 | -1.38 | 0.66 |  |  |  | 1.48
TR Hradec T402 | 27T-TR-HRAT402-B | CEPS |  |  | 723 | 400 | 231 | 0.33 | 38.23 | -0.6 | 0.5 |  |  |  | 1.48
TR Prosenice T401 | 27T-TR-PRNT401X5 | CEPS |  |  | 722 | 400 | 231 | 0.43 | 37.82 | -15.61 | 0.62 |  |  |  | 1.48
TR Sokolnice T401 | 27T-TR-SOKT401-H | CEPS |  |  | 722 | 400 | 231 | 0.48 | 42.29 | -15.61 | 0.65 |  |  |  | 1.48
PST Hradec 1 | 27T-HRD4T451---Y | CEPS |  |  | 1168 | 400 | 400 | 0.21 | 25.5 | -24.07 | 1.06 | <-6;6> | 90 | symmetrical |  | 1.63 | connected to tieline 10T-CZ-DE-00002U
PST Hradec 2 | 27T-HRD4T452---T | CEPS |  |  | 1168 | 400 | 400 | 0.21 | 25.59 | -24.07 | 1.07 | <-6;6> | 90 | symmetrical |  | 1.63 | connected to tieline 10T-CZ-DE-00002U
PST Hradec 3 | 27T-HRD4T453---O | CEPS |  |  | 1168 | 400 | 400 | 0.21 | 25.44 | -24.07 | 1.08 | <-6;6> | 90 | symmetrical |  | 1.63 | connected to tieline 10T-CZ-DE-00003S
PST Hradec 4 | 27T-HRD4T454---J | CEPS |  |  | 1168 | 400 | 400 | 0.2 | 25.63 | -24.07 | 1.08 | <-6;6> | 90 | symmetrical |  | 1.63 | connected to tieline 10T-CZ-DE-00003S
TR Bericevo 421 | 11T0-0000-0082-R | ELES |  |  | 1000 | 400 | 231 | 0.1868 | 15.754 | -14.0161 | 2.5299
PST Divaca | 28T-0000001569-4, 28T-0000001568-7 | ELES |  |  | 1732 | 400 | 400 | 0.2 | 24.489 | -5.166 | 0.938 |  | 90 | Symetrical |  | 2.27 | Two transformers in parallel, modelled as one (EICs: 28T-0000001569-4, 28T-0000001568-7), used as RA in CSE CCR. Line connected to PST is Divaca - Redipuglia 400 kV (SI-IT tieline)
TR Podlog 421 | 28T-0000002374-J | ELES |  |  | 1000 | 400 | 231 | 0.1734 | 15.807 | -9.4238 | 2.4812
TR Divaca 211 | 28T-0000001565-G | ELES |  |  | 753 | 220 | 115 | 0.2998 | 12.031 | -62.7778 | 9.656
TR Divaca 212 | 28T-0000001566-D | ELES |  |  | 753 | 220 | 115 | 0.3703 | 11.65 | -62.7778 | 9.656
TR Divaca 411 | 28T-0000001567-A | ELES |  |  | 1506 | 400 | 115 | 0.0749 | 5.8891 | -10.9223 | 8.121
TR Divaca 412 | 28T0000000002349 | ELES |  |  | 1506 | 400 | 115 | 0.0793 | 5.8758 | -7.7999 | 8.2344
TR AUBANGE PST 1 | 22T20211201AF--4 | ELIA | 1525.3452 | 1686.9082 |  | 243 | 243 | 0.10825 | 9.8409 | -5.0692 | 1.4903 | 0 | 90 | Symmetrical |  | 1.87 | CONNECTED TO AUBANGE – MOULAINE 220.513
TR VAN EYCK PST 1 | 22T-BE-PST--001W | ELIA | 2042.3766 | 2329.6083 |  | 400 | 400 | 0.084256 | 10.5011 | -2.0201 | 1.2216 | -8;8 | 90 | Symmetrical |  | 1.4712 | CONNECTED TO MAASBRACHT – VAN EYCK BLACK/27
TR VAN EYCK PST 2 | 22T-BE-PST--002U | ELIA | 2042.3766 | 2329.6083 |  | 400 | 400 | 0.083808 | 10.4898 | -0.39717 | 1.1773 | -8;8 | 90 | Symmetrical |  | 1.4712 | CONNECTED TO MAASBRACHT – VAN EYCK WHITE/28
TR ZANDVLIET PST 1 | 22T-BE-PST--003S | ELIA | 2042.3766 | 2329.6083 |  | 400 | 400 | 0.08648 | 10.6396 | -2.0395 | 1.1924 | -8;8 | 90 | Symmetrical |  | 1.4712 | CONNECTED TO RILLAND – ZANDVLIET WHITE/30
TR ZANDVLIET PST 2 | 22T20161020---56 | ELIA | 2042.3766 | 2329.6083 |  | 400 | 400 | 0.08648 | 10.6396 | -2.0395 | 1.1924 | -8;8 | 90 | Symmetrical |  | 1.4712 | CONNECTED TO RILLAND – ZANDVLIET GREY/29
TR SCHIFFLANGE PST 1 | 22T20161013----7 | ELIA | 963.0694 | 1051.5145 |  | 235 | 235 | 0.086289 | 7.3168 | -1.4486 | 1.0865 | 0 | 90 | Symmetrical |  | 1.17 | CONNECTED BETWEEN Y – SCHIFFLANGE (– AUBANGE – SANEM) 220.512 AND SCHIFFLANGE – SCHIFFLANGE 220.1
TR MONCEAU PST 1 | 22T-BE-PST--004Q | ELIA | 1027.6835 | 1122.0626 |  | 245 | 160 | 0.24249 | 16.1847 | -6.5641 | 1.1962 | 0 | 90 | Symmetrical |  | 1.667 | CONNECTED TO CHOOZ – MONCEAU 220.48
TR AUBANGE 380/220 TFO 1 | 22T20211201T---A | ELIA | 424.3524 | 463.3236 |  | 400 | 245.42 | 1.1259 | 82.2323 | -1.8058 | 0.5048 | [5 empty] | 3-winding transformer (more info in extra sheet)
TR AUBANGE 380/220 TFO 2 | 22T20211201V---0 | ELIA | 424.3524 | 463.3236 |  | 400 | 245.46 | 1.0082 | 80.527 | -1.8021 | 0.5176 | [5 empty] | 3-winding transformer (more info in extra sheet)
TR BRUME 380/220 TFO 1 | 22T20211201W---W | ELIA | 424.3524 | 463.3236 |  | 400 | 245.42 | 1.1207 | 82.1257 | -2.0008 | 0.5006 | [5 empty] | 3-winding transformer (more info in extra sheet)
TR LIXHE 380/220 TFO 11 | 22T20211201X---R | ELIA | 424.3524 | 463.3236 |  | 400 | 245.596 | 0.99837 | 78.0683 | -0.71816 | 0.2162 | [5 empty] | 3-winding transformer (more info in extra sheet)
TR LIXHE 380/220 TFO 6 | 22T20211201Y---M | ELIA | 424.3524 | 463.3236 |  | 400 | 245.596 | 0.99752 | 77.9456 | -0.69956 | 0.213 | [5 empty] | 3-winding transformer (more info in extra sheet)
TR RIMIERE 380/220 TFO 8 | 22T20211201Z---H | ELIA | 424.3524 | 463.3236 |  | 400 | 245.46 | 1.0181 | 77.7533 | -3.1429 | 0.5313 | [5 empty] | 3-winding transformer (more info in extra sheet)
TR RIMIERE 380/220 TFO 9 | 22T20211201AA--O | ELIA | 424.3524 | 463.3236 |  | 400 | 245.42 | 1.1259 | 82.2323 | -1.8058 | 0.5048 | [5 empty] | 3-winding transformer (more info in extra sheet)
TR STEVIN 380/220 TFO 3 | 22T20211201AB--K | ELIA | 848.7049 | 926.6472 |  | 400 | 225 | 0.36669 | 39.7583 | -0.63121 | 0.4051 | [5 empty] | 3-winding transformer (more info in extra sheet)
TR STEVIN 380/220 TFO 4 | 22T20211201AC--G | ELIA | 848.7049 | 926.6472 |  | 400 | 225 | 0.37038 | 39.8649 | -2.2136 | 0.4031 | [5 empty] | 3-winding transformer (more info in extra sheet)
TR STEVIN 380/220 TFO 5 | 22T20211201AD--C | ELIA | 848.7049 | 926.6472 |  | 400 | 225 | 0.36693 | 39.8383 | -0.11949 | 0.3948 | [5 empty] | 3-winding transformer (more info in extra sheet)
TR STEVIN 380/220 TFO 6 | 22T20211201AE--8 | ELIA | 848.7049 | 926.6472 |  | 400 | 225 | 0.3629 | 39.785 | -0.63474 | 0.3995 | [5 empty] | 3-winding transformer (more info in extra sheet)
TR 1 400/220 Konjsko | 31T-0000-B-0004S | HOPS | 1000 | 1000 |  | 400 | 231 | 0.194 | 15.6 | -8.66 | 2.4 |  | 0 | Asymmetrical | 5 | 0
TR 2 400/220 Konjsko | 31T-0000-B-0005Q | HOPS | 1000 | 1000 |  | 400 | 231 | 0.195 | 15.6 | -7.9 | 2.4 |  | 0 | Asymmetrical | 5 | 0
TR1 400/220 kV Melina | 31T-0000-B-0002W | HOPS | 1000 | 1000 |  | 400 | 231 | 0.196 | 15.5 | -9.42 | 2.5 |  | 0 | Asymmetrical | 5 | 0
TR2 400/220 kV Melina | 31T-0000-B-0003U | HOPS | 1000 | 1000 |  | 400 | 231 | 0.207 | 15.9 | -5.49 | 2.4 |  | 0 | Asymmetrical | 5 | 0
TR4 400/220 kV Zerjavinec | 31T-0000-B-0001Y | HOPS | 1000 | 1000 |  | 400 | 231 | 0.195 | 16.3 | -32.21 | 1.2 | -12;12 | 0 | Symmetrical/Asymmetrical | 0/1,5 | 0,9/0 | usually works in asymmetrical mode
TR Sajoszoged TR3 | 15T-M0000001145Z | MAVIR | 1250 | 1250 |  | 231 | 400 | 0.251 | 12.81 | -18 | 0
TR Martonvasar TR1 | 15T-M0000000817H | MAVIR | 1250 | 1250 |  | 231 | 400 | 0.167 | 12.67 | -1 | 0
TR Martonvasar TR2 | 15T-M0000000818F | MAVIR | 1250 | 1250 |  | 231 | 400 | 0.224 | 13.32 | -18 | 0
TR BYCZYNA-A1 | 19T1100000064579 | PSE | 500 | 500 |  | 400 | 220 | 0.121 | 12.032 | -1.9421 | 0 |  | 0 | Asymmetrical | 1.01 | 0
TR BYCZYNA-A2 | 19T1100000064587 | PSE | 500 | 500 |  | 400 | 220 | 0.121 | 12.032 | -1.9421 | 0 |  | 0 | Asymmetrical | 1.01 | 0
TR DUNOWO-A1 | 19T0000000035667 | PSE | 400 | 400 |  | 400 | 220 | 0.2468 | 13.504 | -11.1777 | 0 |  | 0 | Asymmetrical | 0.722 | 0
TR GDANSK-A3 | 19T110000006503S | PSE | 330 | 330 |  | 400 | 220 | 0.1936 | 18.905 | -8.3471 | 0 |  | 0 | Asymmetrical | 1.01 | 0
PST GRUDZIADZ-A3 | 19T110000006511T | PSE | 500 | 500 |  | 400 | 220 | 0.15 | 12.487 | -7.7273 | 0 |  | 90 | Symmetrical | 0 | 0.758 | Change of tap position of phase shifting transformer (400/220) in substation Grudziadz
TR JOACHIMOW-A1 | 19T110000006523M | PSE | 500 | 500 |  | 400 | 220 | 0.1162 | 11.393 | -2.376 | 0 |  | 0 | Asymmetrical | 1.01 | 0
TR JOACHIMOW-A2 | 19T110000006524K | PSE | 500 | 500 |  | 400 | 220 | 0.1162 | 11.597 | -6.2603 | 0 |  | 0 | Asymmetrical | 1.01 | 0
PST JOACHIMOW-TD1 | 19T110000006525I | PSE | 500 | 500 |  | 220 | 220 | 0.0678 | 0.9874 | -2.7273 | 0 |  | 90 | Symmetrical | 0 | 1.458 | Change of tap position of phase shifting transformer (400/220) in substation Joachimow
PST JOACHIMOW-TD2 | 19T110000006526G | PSE | 500 | 500 |  | 220 | 220 | 0.0678 | 0.997 | -2.8306 | 0 |  | 90 | Symmetrical | 0 | 1.458 | Change of tap position of phase shifting transformer (400/220) in substation Joachimow
TR KIELCE-A1 | 19T110000006530P | PSE | 500 | 500 |  | 400 | 220 | 0.1452 | 11.722 | -3.3678 | 0 |  | 0 | Asymmetrical | 1.263 | 0
TR KOZIENICE-A2 | 19T110000006540M | PSE | 500 | 500 |  | 400 | 220 | 0.1742 | 11.084 | -3.7603 | 0 |  | 0 | Asymmetrical | 1.263 | 0
TR KRAJNIK-A2 | 19T000000003616I | PSE | 400 | 400 |  | 400 | 220 | 0.2226 | 13.741 | -38.4917 | 0 |  | 0 | Asymmetrical | 1.147 | 0
TR KRAJNIK-A3 | 19T000000003617G | PSE | 500 | 500 |  | 400 | 220 | 0.1258 | 12.874 | -3.0785 | 0 |  | 0 | Asymmetrical | 1.01 | 0
TR LAGISZA-A2 | 19T1100000065478 | PSE | 500 | 500 |  | 400 | 220 | 0.1258 | 12.797 | -5.6612 | 0 |  | 0 | Asymmetrical | 1.01 | 0
TR MIKULOWA-A1 | 19T000000004057N | PSE | 500 | 500 |  | 400 | 220 | 0.1065 | 9.438 | -3.5124 | 0 |  | 0 | Asymmetrical | 1.124 | 0
TR MIKULOWA-A2 | 19T000000004058L | PSE | 500 | 500 |  | 400 | 220 | 0.1065 | 9.438 | -3.5124 | 0 |  | 0 | Asymmetrical | 1.124 | 0
PST MIKULOWA-PF1 | 19T0000000063830 | PSE | 1200 | 1200 |  | 400 | 400 | 0.112 | 11.616 | -34.6375 | 0 | -8;8 | 90 | Symmetrical | 0 | 1.108 | Change of tap position of phase shifting transformer (400) on line Mikulowa-Hagenwerder
PST MIKULOWA-PF2 | 19T000000006384Z | PSE | 1200 | 1200 |  | 400 | 400 | 0.112 | 11.632 | -34.6625 | 0 | -8;8 | 90 | Symmetrical | 0 | 1.108 | Change of tap position of phase shifting transformer (400) on line Mikulowa-Hagenwerder
PST MIKULOWA-PF3 | 19T000000006385X | PSE | 1200 | 1200 |  | 400 | 400 | 0.112 | 11.6 | -34.6375 | 0 | -8;8 | 90 | Symmetrical | 0 | 1.108 | Change of tap position of phase shifting transformer (400) on line Mikulowa-Hagenwerder
PSTMIKULOWA-PF4 | 19T000000006386V | PSE | 1200 | 1200 |  | 400 | 400 | 0.112 | 11.568 | -34.7 | 0 | -8;8 | 90 | Symmetrical | 0 | 1.108 | Change of tap position of phase shifting transformer (400) on line Mikulowa-Hagenwerder
PST MIKULOWA-TD1 | 19T110000006561E | PSE | 500 | 500 |  | 220 | 220 | 0.0968 | 0.8712 | -2.5 | 0 | -5;5 | 90 | Symmetrical | 0 | 1.458 | Change of tap position of phase shifting transformer (400/220) in substation Mikulowa
PST MIKULOWA-TD2 | 19T110000006562C | PSE | 500 | 500 |  | 220 | 220 | 0.0968 | 0.8712 | -2.5 | 0 | -5;5 | 90 | Symmetrical | 0 | 1.458 | Change of tap position of phase shifting transformer (400/220) in substation Mikulowa
TR MILOSNA-A3 | 19T1100000065648 | PSE | 400 | 400 |  | 400 | 220 | 0.2565 | 13.286 | -27.4587 | 0 |  | 0 | Asymmetrical | 0 | 0
TR OLSZTYN-MATK-A3 | 19T1100000065818 | PSE | 330 | 330 |  | 400 | 220 | 0.1839 | 18.169 | -8.6364 | 0 |  | 0 | Asymmetrical | 1.01 | 0
TR OLTARZEW-A1 | 19T1100000065842 | PSE | 500 | 500 |  | 400 | 220 | 0.1258 | 11.5 | -2.9752 | 0 |  | 0 | Asymmetrical | 1.01 | 0
TR OLTARZEW-A2 | 19T1100000065850 | PSE | 500 | 500 |  | 400 | 220 | 0.1258 | 11.51 | -2.7893 | 0 |  | 0 | Asymmetrical | 1.01 | 0
TR OSTROLEKA-A1 | 19T000000006378U | PSE | 500 | 500 |  | 400 | 220 | 0.121 | 11.277 | -2.8512 | 0 |  | 0 | Asymmetrical | 1.01 | 0
TR PATNOW-A2 | 19T110000006597U | PSE | 500 | 500 |  | 400 | 220 | 0.1452 | 12.845 | -6.5289 | 0 |  | 0 | Asymmetrical | 1.035 | 0
TR POLANIEC-A2 | 19T110000006601S | PSE | 400 | 400 |  | 400 | 220 | 0.271 | 14.757 | -25.9091 | 0 |  | 0 | Asymmetrical | 0.722 | 0
TR POLKOWICE-A3 | 19T0000000064187 | PSE | 500 | 500 |  | 400 | 220 | 0.1162 | 11.437 | -3.0992 | 0 |  | 0 | Asymmetrical | 1.01 | 0
TR ROGOWIEC-A1 | 19T110000006626C | PSE | 500 | 500 |  | 400 | 220 | 0.1549 | 12.458 | -1.6736 | 0 |  | 0 | Asymmetrical | 0 | 0
TR ROGOWIEC-A2 | 19T110000006627A | PSE | 500 | 500 |  | 400 | 220 | 0.121 | 12.115 | -2.4587 | 0 |  | 0 | Asymmetrical | 1.01 | 0
TR RZESZOW-A3 | 19T110000006633F | PSE | 1251 | 1251 |  | 750 | 400 | 0.096 | 19.264 | -4.6437 | 0 |  | 0 | Asymmetrical | 0.473 | 0
TR RZESZOW-A4 | 19T110000006634D | PSE | 1251 | 1251 |  | 750 | 400 | 0.096 | 19.248 | -4.65 | 0 |  | 0 | Asymmetrical | 0.471 | 0
TR SWIEBODZICE-A3 | 19T000000003947W | PSE | 500 | 500 |  | 400 | 220 | 0.121 | 12.371 | -2.6033 | 0 |  | 0 | Asymmetrical | 1.01 | 0
TR WIELOPOLE-A3 | 19T000000003959P | PSE | 400 | 400 |  | 400 | 220 | 0.2904 | 15.711 | -24.3182 | 0 |  | 0 | Asymmetrical | 1.279 | 0
TR 400/225kV 762 ALBERTVILLE | 17T000000014478N | RTE | 1659 | 1803 |  | 400 | 225 | 0.24 | 43.1
TR 400/225kV 763 ALBERTVILLE | 17T000000016016E | RTE | 1575 | 1803 |  | 400 | 225 | 0.11 | 45.9
TR 400/225kV 761 ARGIA (BAYONNE SUD) | 17T-FR-00000065R | RTE | 1659 | 1803 |  | 400 | 225 | 0.17 | 42.4
TR 400/225kV 761 ARGOEUVES | 17T000000014153E | RTE | 1659 | 1803 |  | 400 | 225 | 0.28 | 45.2
TR 400/225kV 763 ARGOEUVES | 17T000000014154C | RTE | 1659 | 1803 |  | 400 | 225 | 0.31 | 46.2
TR 400/225kV 761 ATTAQUES (LES) | 17T000000014162D | RTE | 847 | 921 |  | 400 | 225 | 0.01 | 74.3
TR 400/225kV 762 ATTAQUES (LES) | 17T000000014163B | RTE | 847 | 921 |  | 400 | 225 | 0.37 | 68.1
TR 400/225kV 761 AVELIN | 17T0000000141738 | RTE | 1659 | 1803 |  | 400 | 225 | 0.29 | 45.7
TR 400/225kV 762 AVELIN | 17T0000000141746 | RTE | 1659 | 1803 |  | 400 | 225 | 0.28 | 45.2
TR 400/225kV 763 AVELIN | 17T0000000141754 | RTE | 1659 | 1803 |  | 400 | 225 | 0.28 | 45.4
TR 400/225kV 761 AVOINE (POSTE 400 KV) | 17T0000000145075 | RTE | 840 | 913 |  | 400 | 225 | 0.51 | 69.4
TR 400/225kV 761 BROC-CARROS (LE) | 17T000000014510G | RTE | 1659 | 1803 |  | 400 | 225 | 0.1 | 42.3
TR 400/225kV 762 BROC-CARROS (LE) | 17T000000014511E | RTE | 1659 | 1803 |  | 400 | 225 | 0.26 | 45.5
TR 400/225kV 761 BEAUMONT-MONTEUX | 17T0000000145237 | RTE | 1659 | 1803 |  | 400 | 225 | 0.23 | 45.3
TR 400/225kV 762 BEAUMONT-MONTEUX | 17T0000000145245 | RTE | 1659 | 1803 |  | 400 | 225 | 0.25 | 45.4
TR 400/225kV 761 BAIXAS | 17T0000000145326 | RTE | 829 | 901 |  | 400 | 225 | 2.2643 | 74.1
TR 400/225kV 762 BAIXAS | 17T0000000145334 | RTE | 829 | 901 |  | 400 | 225 | 2.3134 | 73.8
TR 400/225kV 763 BAIXAS | 17T000000015933K | RTE | 830 | 902 |  | 400 | 225 | -0.029 | 73.15
TR 400/225kV 761 BAYET | 17T000000014547U | RTE | 847 | 921 |  | 400 | 225 | 0.62 | 70
TR 400/225kV 762 BAYET | 17T000000014548S | RTE | 775 | 910 |  | 400 | 225 | 0.71 | 70.5
TR 400/225kV 763 BAYET | 17T000000014549Q | RTE | 795 | 921 |  | 400 | 225 | 0.68 | 70.6
TR 400/225kV 761 BEZAUMONT | 17T000000014558P | RTE | 847 | 921 |  | 400 | 225 | 0.16 | 70.6
TR 400/225kV 762 BEZAUMONT | 17T000000014559N | RTE | 847 | 921 |  | 400 | 225 | 0.15 | 71.3
TR 400/225kV 761 BIANCON | 17T000000014564U | RTE | 1620 | 1803 |  | 400 | 225 | 0.24 | 43.1
TR 400/225kV 762 BIANCON | 17T000000014565S | RTE | 1620 | 1803 |  | 400 | 225 | 0.24 | 43.1
TR 400/225kV 761 BOISSE (LA) | 17T000000014572V | RTE | 1659 | 1803 |  | 400 | 225 | 0.07 | 42.4
TR 400/225kV 762 BOISSE (LA) | 17T000000014573T | RTE | 1659 | 1803 |  | 400 | 225 | 0.1 | 39.8
TR 400/225kV 761 BOUTRE | 17T000000014581U | RTE | 1659 | 1803 |  | 400 | 225 | 0.08 | 42.3
TR 400/225kV 762 BOUTRE | 17T000000014582S | RTE | 1620 | 1800 |  | 400 | 225 | 0.09 | 42.6
TR 400/225kV 761 BRAUD | 17T000000014583Q | RTE | 884 | 961 |  | 400 | 225 | 0.05 | 70.3
TR 400/225kV 762 BREUIL (LE) | 17T000000014586K | RTE | 847 | 921 |  | 400 | 225 | 0.4 | 68.6
TR 400/225kV 761 CALAN | 17T000000016006H | RTE | 1540 | 1803 |  | 400 | 225 | 0.082 | 45.95
TR 400/225kV 761 CANTEGRIT | 17T-FR-000000422 | RTE | 1659 | 1803 |  | 400 | 225 | 0.09 | 42.5
TR 400/225kV 762 CANTEGRIT | 17T-FR-000000430 | RTE | 1659 | 1803 |  | 400 | 225 | 0.06 | 42.7
TR 400/225kV 761 CAPELLE (LA) | 17T000000016043B | RTE | 1445 | 1803 |  | 400 | 225 | 0.087 | 45.77
TR 400/225kV 761 CAZARIL | 17T0000000146063 | RTE | 847 | 921 |  | 400 | 225 | 0.43 | 69.9
TR 400/225kV 762 CAZARIL | 17T0000000146071 | RTE | 810 | 847 |  | 400 | 225 | 0.55 | 68.9
TR 400/225kV 761-(769) CERGY | 17T000000014198T | RTE | 814 | 850 |  | 400 | 225 | 0.59 | 68.7
TR 400/225kV 763 CERGY | 17T000000014199R | RTE | 1655 | 1800 |  | 400 | 225 | 0.24 | 45.4
TR 400/225kV 764 CERGY | 17T000000014200V | RTE | 1655 | 1800 |  | 400 | 225 | 0.27 | 45.9
TR 400/225kV 765 CERGY | 17T000000014201T | RTE | 1600 | 1800 |  | 400 | 225 | 0.26 | 45.2
TR 400/225kV 769 CERGY | 17T000000014198T | RTE | 850 | 925 |  | 400 | 225 | 0.57 | 72.8
TR 400/225kV 761 CHAINGY | 17T000000014617Z | RTE | 1655 | 1800 |  | 400 | 225 | 0.23 | 45.2
TR 400/225kV 762 CHAINGY | 17T000000014618X | RTE | 1655 | 1800 |  | 400 | 225 | 0.25 | 44.7
TR 400/225kV 761 CHARPENAY | 17T000000014626Y | RTE | 847 | 921 |  | 400 | 225 | 0.57 | 71.2
TR 400/225kV 762 CHARPENAY | 17T000000014627W | RTE | 847 | 921 |  | 400 | 225 | 0.05 | 70.9
TR 400/225kV 761 CHESNOY (LE) | 17T000000014210S | RTE | 1659 | 1803 |  | 400 | 225 | 0.14 | 42.3
TR 400/225kV 762 CHESNOY (LE) | 17T000000014211Q | RTE | 847 | 921 |  | 400 | 225 | 0.08 | 42.4
TR 400/225kV 763 CHESNOY (LE) | 17T000000016084Y | RTE | 1659 | 1803 |  | 400 | 225 | 0.126 | 45.66
TR 400/225kV 761 CIROLLIERS | 17T000000014215I | RTE | 1659 | 1803 |  | 400 | 225 | 0.32 | 45.7
TR 400/225kV 762 CIROLLIERS | 17T000000014216G | RTE | 1659 | 1803 |  | 400 | 225 | 0.28 | 45.8
TR 400/225kV 763 CIROLLIERS | 17T000000014217E | RTE | 1659 | 1803 |  | 400 | 225 | 0.25 | 45.8
TR 400/225kV 761 CORDEMAIS-POSTE | 17T000000014652X | RTE | 1659 | 1803 |  | 400 | 225 | 0.29 | 45.8
TR 400/225kV 763 CORDEMAIS-POSTE | 17T000000014653V | RTE | 1659 | 1803 |  | 400 | 225 | 0.07 | 42.4
TR 400/225kV 765 CORDEMAIS-POSTE | 17T000000014654T | RTE | 847 | 921 |  | 400 | 225 | 0.7 | 70.4
TR 400/225kV 769 CORDEMAIS-POSTE | 17T000000014655R | RTE | 847 | 921 |  | 400 | 225 | 0.43 | 63
TR 400/225kV 761 CORNIER | 17T000000014663S | RTE | 1659 | 1803 |  | 400 | 225 | 0.28 | 45.5
TR 400/225kV 762 CORNIER | 17T000000014664Q | RTE | 1630 | 1803 |  | 400 | 225 | 0.27 | 45.7
TR 400/225kV 761 CHAMPAGNIER | 17T000000014676J | RTE | 1659 | 1803 |  | 400 | 225 | 0.11 | 42.4
TR 400/225kV 762 CHAMPAGNIER | 17T000000014677H | RTE | 1659 | 1803 |  | 400 | 225 | 0.09 | 42.6
TR 400/225kV 765 CRENEY | 17T000000014685I | RTE | 845 | 884 |  | 400 | 225 | 0.35 | 45.4
TR 400/225kV 766 CRENEY | 17T000000014686G | RTE | 847 | 885 |  | 400 | 225 | 0.37 | 36.5
TR 400/225kV 768 CRENEY | 17T000000014687E | RTE | 1659 | 1803 |  | 400 | 225 | 0.11 | 42.4
TR 400/225kV 761 CUBNEZAIS | 17T000000014694H | RTE | 1655 | 1800 |  | 400 | 225 | 0.29 | 44.8
TR 400/225kV 762 CUBNEZAIS | 17T000000014695F | RTE | 1655 | 1800 |  | 400 | 225 | 0.05 | 42.4
TR 400/225kV 761 DAMBRON | 17T0000000147051 | RTE | 1655 | 1800 |  | 400 | 225 | 0.09 | 42.4
TR 400/225kV 760 DISTRE | 17T0000000147132 | RTE | 1659 | 1803 |  | 400 | 225 | 0.05 | 42.5
TR 400/225kV 762 DISTRE | 17T000000014715Z | RTE | 840 | 913 |  | 400 | 225 | 0.57 | 72.8
TR 400/225kV 765 DISTRE | 17T000000014716X | RTE | 849 | 923 |  | 400 | 225 | 0.15 | 74.8
TR 400/225kV 766 DISTRE | 17T000000014717V | RTE | 1659 | 1803 |  | 400 | 225 | 0.03 | 42.4
TR 400/225kV 764 DOMLOUP | 17T000000014725W | RTE | 1659 | 1803 |  | 400 | 225 | 0.25 | 43.7
TR 400/225kV 765 DOMLOUP | 17T000000014726U | RTE | 1659 | 1803 |  | 400 | 225 | 0.09 | 42.6
TR 400/225kV 762 DONZAC | 17T000000014727S | RTE | 1659 | 1803 |  | 400 | 225 | 0.13 | 42.2
TR 400/225kV 761 ECHALAS | 17T000000014734V | RTE | 1659 | 1803 |  | 400 | 225 | 0.27 | 45.7
TR 400/225kV 762 ECHALAS | 17T000000014735T | RTE | 1659 | 1803 |  | 400 | 225 | 0.07 | 42.5
TR 400/225kV 761 EGUZON | 17T000000014738N | RTE | 1659 | 1803 |  | 400 | 225 | 0.27 | 44.8
TR 400/225kV 762 EGUZON | 17T000000014739L | RTE | 847 | 921 |  | 400 | 225 | 0.25 | 68.3
TR 400/225kV 761 FEUILLANE | 17T000000014784G | RTE | 1659 | 1803 |  | 400 | 225 | 0.111 | 39.8
TR 400/225kV 761 FRASNE | 17T000000014141L | RTE | 830 | 902 |  | 400 | 225 | 0.004 | 74.25
TR 400/225kV 761 GRANDE-ILE | 17T000000014818P | RTE | 847 | 921 |  | 400 | 225 | 0.02 | 70.6
TR 400/225kV 762 GRANDE-ILE | 17T000000014819N | RTE | 815 | 921 |  | 400 | 225 | 0.45 | 71.2
TR 400/225kV 761 GALOREAUX (LES) | 17T000000016003N | RTE | 1659 | 1803 |  | 400 | 225 | 0.119 | 39.64
TR 400/225kV 761 GAUDIERE (LA) | 17T000000014850T | RTE | 847 | 921 |  | 400 | 225 | 0.86 | 74.5
TR 400/225kV 762 GAUDIERE (LA) | 17T000000014851R | RTE | 1660 | 1805 |  | 400 | 225 | 0.07 | 42.7
TR 400/225kV 761 GAVRELLE | 17T0000000142718 | RTE | 1659 | 1803 |  | 400 | 225 | 0.12 | 42.2
TR 400/225kV 761 GENISSIAT-POSTE | 17T000000014853N | RTE | 1659 | 1803 |  | 400 | 225 | 0.03 | 42.3
TR 400/225kV 762 GENISSIAT-POSTE | 17T000000014854L | RTE | 1540 | 1803 |  | 400 | 225 | 0.33 | 42.3
TR 400/225kV 761 GRANZAY | 17T0000000148876 | RTE | 1659 | 1803 |  | 400 | 225 | 0.19 | 44.9
TR 400/225kV 762 GRANZAY | 17T0000000148884 | RTE | 1659 | 1803 |  | 400 | 225 | 0.24 | 45
TR 400/225kV 763 GRANZAY | 17T0000000148892 | RTE | 1659 | 1803 |  | 400 | 225 | 0.31 | 45.6
TR 400/225kV 761 GROSNE | 17T0000000148965 | RTE | 1659 | 1803 |  | 400 | 225 | 0.23 | 45
TR 400/225kV 762 GROSNE | 17T0000000148973 | RTE | 1659 | 1803 |  | 400 | 225 | 0.1 | 45.4
TR 400/225kV 762 HENRI-PAUL | 17T000000014135G | RTE | 1660 | 1805 |  | 400 | 225 | 0.087 | 45.55
TR 400/225kV 762 HAVRE (LE) (POSTE) | 17T0000000142815 | RTE | 1659 | 1803 |  | 400 | 225 | 0.11 | 42.5
TR 400/225kV 763 HAVRE (LE) (POSTE) | 17T0000000142823 | RTE | 1659 | 1803 |  | 400 | 225 | 0.06 | 42.3
TR 400/225kV 761 JONQUIERES | 17T000000014991B | RTE | 1659 | 1803 |  | 400 | 225 | 0.28 | 45.4
TR 400/225kV 762 JONQUIERES | 17T0000000149929 | RTE | 1659 | 1803 |  | 400 | 225 | 0.29 | 45.6
TR 400/225kV 761 JUMEAUX (LES) | 17T0000000149961 | RTE | 847 | 921 |  | 400 | 225 | 0.1 | 70.1
TR 400/225kV 762 JUMEAUX (LES) | 17T000000014998Y | RTE | 847 | 921 |  | 400 | 225 | 0.44 | 69.3
TR 400/225kV 761 LATENA | 17T000000014287U | RTE | 1659 | 1803 |  | 400 | 225 | 0.26 | 45.5
TR 400/225kV 762 LATENA | 17T000000014288S | RTE | 1659 | 1803 |  | 400 | 225 | 0.27 | 45
TR 400/225kV 763 LATENA | 17T000000014289Q | RTE | 1659 | 1803 |  | 400 | 225 | 0.27 | 45.4
TR 400/225kV 763 LAUNAY | 17T000000014295V | RTE | 845 | 918 |  | 400 | 225 | 0.68 | 70.4
TR 400/225kV 761 LESQUIVE | 17T0000000150494 | RTE | 1659 | 1803 |  | 400 | 225 | 0.28 | 45.4
TR 400/225kV 762 LESQUIVE | 17T000000015050J | RTE | 1659 | 1803 |  | 400 | 225 | 0.36 | 46.1
TR 400/225kV 761 LIMEUX | 17T000000016165Y | RTE | 1659 | 1803 |  | 400 | 225 | 0.12 | 39.5
TR 400/225kV 766 LOGELBACH | 17T000000015060G | RTE | 840 | 913 |  | 400 | 225 | 0.64 | 69.9
TR 400/225kV 767 LOGELBACH | 17T000000015061E | RTE | 840 | 913 |  | 400 | 225 | 0.57 | 70.3
TR 400/225kV 761 MAMBELIN | 17T000000015150F | RTE | 840 | 913 |  | 400 | 225 | 0.22 | 70
TR 400/225kV 762 MAMBELIN | 17T000000015151D | RTE | 840 | 913 |  | 400 | 225 | 0.19 | 70.9
TR 400/225kV 763 MAMBELIN | 17T000000015152B | RTE | 840 | 913 |  | 400 | 225 | 0.17 | 68.7
TR 400/225kV 761 MANDARINS | 17T000000014305H | RTE | 847 | 921 |  | 400 | 225 | 0.35 | 73
TR 400/225kV 763 MANDARINS | 17T000000014306F | RTE | 847 | 921 |  | 400 | 225 | 0.35 | 72
TR 400/225kV 761 MARLENHEIM | 17T0000000151555 | RTE | 1659 | 1803 |  | 400 | 225 | 0.06 | 42.4
TR 400/225kV 762 MARLENHEIM | 17T0000000151563 | RTE | 1659 | 1803 |  | 400 | 225 | 0.08 | 44.2
TR 400/225kV 763 MARLENHEIM | 17T0000000151571 | RTE | 1659 | 1803 |  | 400 | 225 | 0.22 | 44.9
TR 400/225kV 761 MARMAGNE | 17T0000000151822 | RTE | 1659 | 1803 |  | 400 | 225 | 0.11 | 45.87
TR 400/225kV 761 MARSILLON | 17T000000016017C | RTE | 1660 | 1805 |  | 400 | 225 | 1.0633 | 45.62
TR 400/225kV 761 MARTYRE (LA) | 17T0000000151911 | RTE | 1659 | 1803 |  | 400 | 225 | 0.28 | 46
TR 400/225kV 762 MARTYRE (LA) | 17T000000015193Y | RTE | 1659 | 1803 |  | 400 | 225 | 0.27 | 45.8
TR 400/225kV 761 MASTAING | 17T000000014314G | RTE | 1659 | 1803 |  | 400 | 225 | 0.29 | 45.6
TR 400/225kV 762 MASTAING | 17T000000014315E | RTE | 1659 | 1803 |  | 400 | 225 | 0.15 | 42.5
TR 400/225kV 761 MAZURES | 17T0000000143196 | RTE | 847 | 921 |  | 400 | 225 | 0.36 | 69.3
TR 400/225kV 762 MAZURES | 17T000000014320L | RTE | 847 | 921 |  | 400 | 225 | 0.73 | 67.6
TR 400/225kV 763 MAZURES | 17T000000014321J | RTE | 1650 | 1803 |  | 400 | 225 | 0.11 | 42.2
TR 400/225kV 761 MEZEROLLES | 17T000000014322H | RTE | 1659 | 1803 |  | 400 | 225 | 0.27 | 45.4
TR 400/225kV 762 MEZEROLLES | 17T000000014323F | RTE | 847 | 921 |  | 400 | 225 | 0.54 | 69.6
TR 400/225kV 763 MEZEROLLES | 17T000000014324D | RTE | 1659 | 1803 |  | 400 | 225 | 0.14 | 42.4
TR 400/225kV 764 MEZEROLLES | 17T000000014325B | RTE | 1659 | 1803 |  | 400 | 225 | 0.28 | 45.5
TR 400/225kV 761 MIONS | 17T000000015225A | RTE | 1659 | 1803 |  | 400 | 225 | 0.14 | 42.4
TR 400/225kV 762 MIONS | 17T0000000152268 | RTE | 1659 | 1803 |  | 400 | 225 | 0.14 | 42
TR 400/225kV 763 MIONS | 17T0000000152276 | RTE | 1630 | 1803 |  | 400 | 225 | 0.22 | 45
TR 400/225kV 761 MORBRAS | 17T0000000143285 | RTE | 1659 | 1803 |  | 400 | 225 | 0.25 | 45.4
TR 400/225kV 762 MORBRAS | 17T0000000143293 | RTE | 1659 | 1803 |  | 400 | 225 | 0.27 | 45.5
TR 400/225kV 763 MORBRAS | 17T000000014330I | RTE | 1659 | 1803 |  | 400 | 225 | 0.28 | 45.2
TR 400/225kV 764 MORBRAS | 17T000000014331G | RTE | 1659 | 1803 |  | 400 | 225 | 0.31 | 45.4
TR 400/225kV 761 MOULAINE | 17T000000015248Z | RTE | 1659 | 1803 |  | 400 | 225 | 0.44 | 36.1
TR 400/225kV 762 MOULAINE | 17T0000000159657 | RTE | 1659 | 1803 |  | 400 | 225 | 0.11 | 42.6
TR 400/225kV 761 MARQUIS (LE) | 17T0000000152535 | RTE | 845 | 884 |  | 400 | 225 | 0.55 | 73.1
TR 400/225kV 762 MARQUIS (LE) | 17T0000000152543 | RTE | 1659 | 1803 |  | 400 | 225 | 0.53 | 73
TR 400/225kV 763 MARQUIS (LE) | 17T0000000152551 | RTE | 845 | 884 |  | 400 | 225 | 0.41 | 62.7
TR 400/225kV 764 MARQUIS (LE) | 17T000000016283S | RTE | 1659 | 1803 |  | 400 | 225 | 0.099 | 40.11
TR 400/225kV 761 NEOULES | 17T000000015293U | RTE | 1659 | 1803 |  | 400 | 225 | 0.13 | 42
TR 400/225kV 762 NEOULES | 17T000000015294S | RTE | 1659 | 1803 |  | 400 | 225 | 0.28 | 45.1
TR 400/225kV 761 OUDON | 17T0000000159754 | RTE | 1659 | 1803 |  | 400 | 225 | 0.14 | 44.8
TR 400/225kV 761 PRAZ-ST-ANDRE | 17T000000015322C | RTE | 847 | 921 |  | 400 | 225 | 0.11 | 67.9
TR 400/225kV 761 PLESSIS-GASSOT | 17T0000000143439 | RTE | 1655 | 1800 |  | 400 | 225 | 0.32 | 45.9
TR 400/225kV 762 PLESSIS-GASSOT | 17T0000000143447 | RTE | 1655 | 1800 |  | 400 | 225 | 0.08 | 42.3
TR 400/225kV 763 PLESSIS-GASSOT | 17T0000000143455 | RTE | 1655 | 1800 |  | 400 | 225 | 0.29 | 45.2
TR 400/225kV 764 PLESSIS-GASSOT | 17T0000000143463 | RTE | 1600 | 1800 |  | 400 | 225 | 0.28 | 44.6
TR 400/225kV 765 PLESSIS-GASSOT | 17T0000000143471 | RTE | 1655 | 1800 |  | 400 | 225 | 0.28 | 45.1
TR 400/225kV 762 PLAINE HAUTE | 17T0000000162077 | RTE | 1659 | 1803 |  | 400 | 225 | 0.098 | 39.63
TR 400/225kV 763 PLAINE HAUTE | 17T000000015330D | RTE | 1659 | 1803 |  | 400 | 225 | 0.31 | 45.8
TR 400/225kV 761 PLAN-D ORGON | 17T000000014136E | RTE | 847 | 921 |  | 400 | 225 | 0.25 | 76.4
TR 400/225kV 761 PONTEAU | 17T0000000154066 | RTE | 1659 | 1803 |  | 400 | 225 | 0.068 | -11.7
TR 400/225kV 761 QUINTES (LES) | 17T000000015449P | RTE | 1659 | 1803 |  | 400 | 225 | 0.18 | 42.9
TR 400/225kV 762 QUINTES (LES) | 17T0000000154503 | RTE | 1660 | 1805 |  | 400 | 225 | 0.11 | 42.3
TR 400/225kV 761 REALTOR | 17T000000015482R | RTE | 1660 | 1805 |  | 400 | 225 | 0.12 | 41.7
TR 400/225kV 762 REALTOR | 17T000000015483P | RTE | 1660 | 1805 |  | 400 | 225 | 0.14 | 42.7
TR 400/225kV 763 REALTOR | 17T000000015484N | RTE | 1660 | 1805 |  | 400 | 225 | 0.11 | 41.8
TR 400/225kV 761 REMISE | 17T000000014138A | RTE | 829 | 901 |  | 400 | 225 | -0.036 | 73.1
TR 400/225kV 764 REVIGNY | 17T000000015487H | RTE | 850 | 925 |  | 400 | 225 | 0.59 | 69.3
TR 400/225kV 765 REVIGNY | 17T000000015938A | RTE | 1659 | 1803 |  | 400 | 225 | 0.09 | 42.8
TR 400/225kV 762 ROUGEMONTIER | 17T000000014393V | RTE | 847 | 921 |  | 400 | 225 | 0.06 | 71.8
TR 400/225kV 763 ROUGEMONTIER | 17T000000014394T | RTE | 1659 | 1803 |  | 400 | 225 | 0.41 | 44.8
TR 400/225kV 765 ROUGEMONTIER | 17T000000014396P | RTE | 1659 | 1803 |  | 400 | 225 | 0.2 | 44.6
TR 400/225kV 761 RUEYRES | 17T0000000155321 | RTE | 829 | 901 |  | 400 | 225 | 0.4 | 69.2
TR 400/225kV 762 RUEYRES | 17T000000015534Y | RTE | 840 | 913 |  | 400 | 225 | 0.52 | 71.6
TR 400/225kV 761 RULHAT | 17T000000015535W | RTE | 847 | 921 |  | 400 | 225 | 0.58 | 70.8
TR 400/225kV 762 RULHAT | 17T000000015536U | RTE | 847 | 921 |  | 400 | 225 | 0.61 | 67.8
TR 400/225kV 763 RULHAT | 17T0000000161291 | RTE | 1659 | 1803 |  | 400 | 225 | 0.103 | 45.77
TR 400/225kV 761 SAUCATS | 17T000000015569F | RTE | 1659 | 1803 |  | 400 | 225 | 0.26 | 45.1
TR 400/225kV 762 SAUCATS | 17T000000015570U | RTE | 1660 | 1805 |  | 400 | 225 | 0.13 | 42.2
TR 400/225kV 763 SAUCATS | 17T000000016008D | RTE | 1659 | 1803 |  | 400 | 225 | 0.167 | 40.43
TR 400/225kV 761 SAUSSET | 17T000000014405D | RTE | 1659 | 1803 |  | 400 | 225 | 0.27 | 43
TR 400/225kV 762 SAUSSET | 17T000000016211G | RTE | 1659 | 1803 |  | 400 | 225 | 0.09 | 45.9
TR 400/225kV 761 SCHEER | 17T000000015574M | RTE | 1659 | 1803 |  | 400 | 225 | 0.118 | 39.27
TR 400/225kV 761 SEREIN | 17T000000015581P | RTE | 1659 | 1803 |  | 400 | 225 | 0.09 | 42.7
TR 400/225kV 762 SEREIN | 17T0000000156026 | RTE | 1659 | 1803 |  | 400 | 225 | 0.12 | 42.7
TR 400/225kV 762 SIERENTZ | 17T000000015606Z | RTE | 840 | 913 |  | 400 | 225 | 0.56 | 69.9
TR 400/225kV 764 SIERENTZ | 17T000000015607X | RTE | 840 | 913 |  | 400 | 225 | 0.62 | 69.9
TR 400/225kV 761 ST-AVOLD | 17T000000015647L | RTE | 1659 | 1803 |  | 400 | 225 | 0.13 | 42.6
TR 400/225kV 765 ST-ELOI | 17T000000015659E | RTE | 810 | 847 |  | 400 | 225 | 0.35 | 68.5
TR 400/225kV 766 ST-ELOI | 17T000000015660T | RTE | 810 | 847 |  | 400 | 225 | 0.07 | 68.3
TR 400/225kV 761 TABARDERIE | 17T000000015732U | RTE | 839 | 912 |  | 400 | 225 | 0.66 | 71
TR 400/225kV 762 TABARDERIE | 17T000000015733S | RTE | 839 | 912 |  | 400 | 225 | 0.64 | 70.6
TR 400/225kV 761 TAMAREAU | 17T000000015737K | RTE | 1659 | 1803 |  | 400 | 225 | 0.25 | 45
TR 400/225kV 762 TAMAREAU | 17T000000015738I | RTE | 1659 | 1803 |  | 400 | 225 | 0.13 | 42.4
TR 400/225kV 763 TAMAREAU | 17T000000015739G | RTE | 1659 | 1803 |  | 400 | 225 | 0.02 | 42.5
TR 400/225kV 763 TAVEL | 17T000000015763J | RTE | 1660 | 1805 |  | 400 | 225 | 0.14 | 42.6
TR 400/225kV 764 TAVEL | 17T000000015764H | RTE | 1660 | 1805 |  | 400 | 225 | 0.15 | 42.5
TR 400/225kV 761 TERRIER | 17T000000014422D | RTE | 1655 | 1800 |  | 400 | 225 | 0.02 | 42.4
TR 400/225kV 762 TERRIER | 17T000000014423B | RTE | 1655 | 1800 |  | 400 | 225 | 0.31 | 45.6
TR 400/225kV 763 TOURBE | 17T000000014432A | RTE | 1661 | 1806 |  | 400 | 225 | 0.24 | 46.2
TR 400/225kV 764 TOURBE | 17T0000000144338 | RTE | 1661 | 1806 |  | 400 | 225 | 0.29 | 45.5
TR 400/225kV 761 TRANS | 17T0000000159665 | RTE | 1560 | 1803 |  | 400 | 225 | 0.09 | 45.9
TR 400/225kV 762 TRANS | 17T0000000159673 | RTE | 1659 | 1803 |  | 400 | 225 | 0.11 | 45.6
TR 400/225kV 761 TRICASTIN-POSTE (LE) | 17T000000018368A | RTE | 2654 | 2654 |  | 400 | 225 | 0.1 | 50.9
TR 400/225kV 762 TRICASTIN-POSTE (LE) | 17T0000000183698 | RTE | 2654 | 2654 |  | 400 | 225 | 0.1 | 50.9
TR 400/225kV 765 TRICASTIN-POSTE (LE) | 17T000000018370N | RTE | 2654 | 2654 |  | 400 | 225 | 0.1 | 50.9
TR 400/225kV 766 TRICASTIN-POSTE (LE) | 17T000000018371L | RTE | 2654 | 2654 |  | 400 | 225 | 0.1 | 50.9
TR 400/225kV 761 VALDIVIENNE | 17T000000015805T | RTE | 847 | 921 |  | 400 | 225 | 0.02 | 68.1
TR 400/225kV 762 VALDIVIENNE | 17T000000015806R | RTE | 847 | 921 |  | 400 | 225 | 0.17 | 69.2
TR 400/225kV 762 VAUPALIERE (LA) | 17T0000000144419 | RTE | 1659 | 1803 |  | 400 | 225 | 0.32 | 45.2
TR 400/225kV 763 VAUPALIERE (LA) | 17T0000000144427 | RTE | 1659 | 1803 |  | 400 | 225 | 0.32 | 45.1
TR 400/225kV 764 VAUPALIERE (LA) | 17T0000000144435 | RTE | 1659 | 1803 |  | 400 | 225 | 0.12 | 42.8
TR 400/225kV 761 VERFEIL | 17T000000015819I | RTE | 1660 | 1805 |  | 400 | 225 | 0.14 | 42.6
TR 400/225kV 762 VERFEIL | 17T000000015820X | RTE | 1660 | 1805 |  | 400 | 225 | 0.14 | 42.1
TR 400/225kV 762 VESLE | 17T0000000144443 | RTE | 1659 | 1803 |  | 400 | 225 | 0.16 | 42.9
TR 400/225kV 763 VESLE | 17T0000000144451 | RTE | 1659 | 1803 |  | 400 | 225 | 0.14 | 43.3
TR 400/225kV 761 VIELMOULIN | 17T000000015848B | RTE | 839 | 912 |  | 400 | 225 | 0.7 | 68.7
TR 400/225kV 762 VIELMOULIN | 17T0000000158499 | RTE | 1659 | 1803 |  | 400 | 225 | 0.25 | 45.2
TR 400/225kV 763 VIELMOULIN | 17T000000015850O | RTE | 839 | 912 |  | 400 | 225 | 0.5 | 69.4
TR 400/225kV 761 VIGY | 17T000000015851M | RTE | 1659 | 1803 |  | 400 | 225 | 0.15 | 42.7
TR 400/225kV 763 VIGY | 17T000000015852K | RTE | 1659 | 1803 |  | 400 | 225 | 0.13 | 42.8
TR 400/225kV 765 VINCEY | 17T000000015857A | RTE | 1659 | 1803 |  | 400 | 225 | 0.09 | 42.4
TR 400/225kV 766 VINCEY | 17T0000000158588 | RTE | 1659 | 1803 |  | 400 | 225 | 0.29 | 45.2
TR 400/225kV 761 VILLEJUST | 17T000000014449U | RTE | 1659 | 1803 |  | 400 | 225 | 0.08 | 42.4
TR 400/225kV 762 VILLEJUST | 17T0000000144508 | RTE | 1659 | 1803 |  | 400 | 225 | 0.1 | 42.4
TR 400/225kV 763 VILLEJUST | 17T0000000144516 | RTE | 1659 | 1803 |  | 400 | 225 | 0.29 | 45.5
TR 400/225kV 764 VILLEJUST | 17T0000000144524 | RTE | 1659 | 1803 |  | 400 | 225 | 0.24 | 45.4
TR 400/225kV 765 VILLEJUST | 17T0000000144532 | RTE | 1659 | 1803 |  | 400 | 225 | 0.3 | 46
TR 400/225kV 766 VILLEJUST | 17T000000016051C | RTE | 1659 | 1803 |  | 400 | 225 | 0.094 | 39.2
TR 400/225kV 762 VILLEVAUDE | 17T000000014457V | RTE | 1659 | 1803 |  | 400 | 225 | 0.27 | 45.8
TR 400/225kV 763 VILLEVAUDE | 17T000000014458T | RTE | 1660 | 1805 |  | 400 | 225 | 0.1 | 42.5
TR 400/225kV 764 VILLEVAUDE | 17T000000014459R | RTE | 1660 | 1805 |  | 400 | 225 | 0.04 | 42.3
TR 400/225kV 765 (769) VILLEVAUDE | 17T0000000144605 | RTE | 1695 | 1842 |  | 400 | 225 | 0.24 | 72
TR 400/225kV 769 VILLEVAUDE | 17T0000000144605 | RTE | 847 | 921 |  | 400 | 225 | 0.34 | 68.1
TR 400/225kV 761 WARANDE | 17T0000000144613 | RTE | 1659 | 1803 |  | 400 | 225 | 0.28 | 44.8
TR 400/225kV 762 WARANDE | 17T0000000144621 | RTE | 1659 | 1803 |  | 400 | 225 | 0.26 | 45.2
TR 400/225kV 763 WARANDE | 17T000000014464Y | RTE | 1659 | 1803 |  | 400 | 225 | 0.33 | 44.3
TR 400/225kV 764 WARANDE | 17T000000014465W | RTE | 1659 | 1803 |  | 400 | 225 | 0.2 | 44.9
TR 400/225kV 761 WEPPES | 17T000000014466U | RTE | 1659 | 1803 |  | 400 | 225 | 0.31 | 46.4
TR 400/225kV 762 WEPPES | 17T000000014467S | RTE | 1659 | 1803 |  | 400 | 225 | 0.27 | 45.7
TR 400/225kV 761 YVELINES-OUEST | 17T000000015900Z | RTE | 1659 | 1803 |  | 400 | 225 | 0.112 | 43.1
TR Krizovany T401 | 24T-KRIZ-T401-02 | SEPS |  |  | 577 | 400 | 231 | 0.486 | 39.197 | -12.4 | 1.3125
TR Bystricany T402 | 24T-BYST-T402-1I | SEPS |  |  | 360 | 400 | 231 | 1.242 | 79.22 | -0.19 | 0.46
TR Bystricany T401 | 24T-BYST-T401-0O | SEPS |  |  | 360 | 400 | 231 | 1.242 | 79.22 | -0.19 | 0.46
PST Arad 400/220 3 | 30T-ARAD400AT3-F | TEL |  |  | 577 | 400 | 231 | 1.02 | 45.988 | -12.368 | 1.8125 | -12;0 | 60 | Asymmetrical |  | 1.25 | Connected in substation 400/220 kV Arad (RO)
TR Bradu 400/220 1 | 30T-BRAD400AT3-3 | TEL |  |  | 577 | 400 | 231 | 0.48 | 45.757 | -2.456 | 0.4688 | 8;0 | 0 | Symmetrical | 1.25
TR Bradu 400/220 2 | 30T-BRAD400AT4-0 | TEL |  |  | 577 | 400 | 231 | 0.48 | 45.757 | -2.456 | 0.4688 | 8;0 | 0 | Symmetrical | 1.25
TR Brazi Vest 400/220 2 | 30T-BRAZ400AT3-R | TEL |  |  | 577 | 400 | 231 | 0.492 | 47.597 | -4.978 | 0.4688 | 8;0 | 0 | Symmetrical | 1.25
TR Bucuresti Sud 400/220 1 | 30T-BUCU400AT3-J | TEL |  |  | 577 | 400 | 231 | 0.51 | 51.997 | -4.962 | 0.6125 | 12;-1 | 0 | Symmetrical | 1.25
TR Bucuresti Sud 400/220 2 | 30T-BUCU400AT4-R | TEL |  |  | 577 | 400 | 231 | 0.51 | 51.997 | -4.962 | 0.6125 | 12;-1 | 0 | Symmetrical | 1.25
TR Gutinas 400/220 1 | 30T-GUTI400AT5-2 | TEL |  |  | 577 | 400 | 231 | 0.656 | 42.514 | -4.985 | 0.3875 | 8;-1 | 0 | Symmetrical | 1.25
TR Gutinas 400/220 2 | 30T-GUTI400AT61W | TEL |  |  | 577 | 400 | 231 | 0.656 | 42.514 | -4.985 | 0.3875 | 8;-1 | 0 | Symmetrical | 1.25
TR Iernut 400/220 1 | 30T-IERN400AT1-U | TEL |  |  | 577 | 400 | 231 | 0.845 | 40.671 | -4.968 | 0.5625 | 7;0 | 0 | Symmetrical | 1.25
TR Lacu Sarat 400/220 1 | 30T-LACS400AT3-Q | TEL |  |  | 577 | 400 | 231 | 0.487 | 47.557 | -4.982 | 0.4269 | 8;-3 | 0 | Symmetrical | 1.25
TR Lacu Sarat 400/220 2 | 30T-LACS400AT4-N | TEL |  |  | 577 | 400 | 231 | 0.4864 | 47.518 | -4.983 | 0.4131 | 8;-3 | 0 | Symmetrical | 1.25
TR Mintia 400/220 1 | 30T-MINT400AT3-T | TEL |  |  | 577 | 400 | 231 | 0.5448 | 47.277 | -4.978 | 0.4688 | 8;-2 | 0 | Symmetrical | 1.25
TR Mintia 400/220 2 | 30T-MINT400AT4-Q | TEL |  |  | 577 | 400 | 231 | 0.5404 | 47.117 | -4.978 | 0.4688 | 8;-2 | 0 | Symmetrical | 1.25
TR Portile de Fier 400/220 1 | 30T-PDFE400AT1-A | TEL |  |  | 721 | 400 | 231 | 0.4608 | 40.637 | -4.33 | 0.625 | 6;0 | 0 | Symmetrical | 1.25
TR Portile de Fier 400/220 2 | 30T-PDFE400AT2-7 | TEL |  |  | 721 | 400 | 231 | 0.4608 | 40.637 | -4.33 | 0.625 | 7;0 | 0 | Symmetrical | 1.25
TR Portile de Fier 400/220 3 | 30T-PDFE400AT3-4 | TEL |  |  | 721 | 400 | 231 | 0.5133 | 40.893 | -6.2226 | 0.5848 | 7;0 | 0 | Symmetrical | 1.25
TR Rosiori 400/220 | 30T-ROSI400AT--1 | TEL |  |  | 577 | 400 | 231 | 0.492 | 47.597 | -4.978 | 0.4688 | 8;0 | 0 | Symmetrical | 1.25
TR Sibiu Sud 400/220 1 | 30T-SIBI400AT5-M | TEL |  |  | 577 | 400 | 231 | 0.602 | 43.675 | -4.986 | 0.375 | 10;0 | 0 | Symmetrical | 1.25
TR Sibiu Sud 400/220 2 | 30T-SIBI400AT6-J | TEL |  |  | 577 | 400 | 231 | 0.602 | 43.675 | -4.986 | 0.375 | 10;0 | 0 | Symmetrical | 1
TR Slatina 400/220 1 | 30T-SLAT400AT1-N | TEL |  |  | 577 | 400 | 231 | 0.7 | 42.793 | -4.985 | 0.3875 | 8;0 | 0 | Symmetrical | 1
TR Slatina 400/220 2 | 30T-SLAT400AT2-K | TEL |  |  | 577 | 400 | 231 | 0.7 | 42.793 | -4.985 | 0.3875 | 8;0 | 0 | Symmetrical | 1.25
PST Urechesti 400/220 1 | 30T-UREC400AT--F | TEL |  |  | 577 | 400 | 231 | 1.02 | 45.988 | -12.368 | 1.8125 | -12;-1 | 60 | Asymmetrical |  | 1.25 | Connected in substation 400/220 kV Urechesti (RO)
TR Iernut 400/220 2 | 30TIERN400AT2--1 | TEL |  |  | 577 | 400 | 231 | 0.512 | 47.196 | -3.5737 | 0.434 | -7;0 | 0 | Symmetrical
PST Meeden PST W |  | TENNET NL | 1520 | 1520 |  | 400 | 400 | 0.1295 | 10.006 | -5.8909 | 2.7701 | -5/5 | 90 | Symmetrical |  | 4.549 | Connected to tie-lie 10T-DE-NL-00002T and 10T-DE-NL-00001V
PST Meeden PST Z |  | TENNET NL | 1520 | 1520 |  | 400 | 400 | 0.1295 | 10.006 | -5.8909 | 2.7701 | -5/5 | 90 | Symmetrical |  | 4.549 | Connected to tie-lie 10T-DE-NL-00002T and 10T-DE-NL-00001V
TR Eemshaven Hogeland 380kV TR 421 | 49T000000000184P | TENNET NL | 1140 | 1140 |  | 400 | 220 | 0.091 | 31.529 | -10.3425 | 0.9695
TR Eemshaven 380kV TR 423 | 49T000000000183R | TENNET NL | 1140 | 1140 |  | 400 | 220 | 0.091 | 31.529 | -10.3425 | 0.9695
TR Eemshaven 380kV TR 401 | 49T000000000181V | TENNET NL | 1140 | 1140 |  | 400 | 220 | 0.0912 | 30.585 | -10.3425 | 0.9695
TR Eemshaven 380kV TR 402 | 49T000000000182T | TENNET NL | 1140 | 1140 |  | 400 | 220 | 0.091 | 31.669 | -10.3425 | 0.9695
TR Ens 380kV TR 404 | 49T000000000187J | TENNET NL | 1140 | 1140 |  | 400 | 220 | 0.1116 | 42.923 | -6.8854 | 0.741
TR Ens 380kV TR 402 | 49T000000000185N | TENNET NL | 760 | 760 |  | 400 | 220 | 0.0912 | 31.462 | -10.3425 | 0.9695
TR Ens 380kV TR 403 | 49T000000000186L | TENNET NL | 760 | 760 |  | 400 | 220 | 0.2117 | 43.136 | -6.9019 | 0.5679
TR Meeden 380kV TR 402 | 49T000000000188H | TENNET NL | 1140 | 1140 |  | 400 | 220 | 0.0626 | 30.653 | -10.3444 | 0.9488
TR Audorf/S T422 | 11T0-0000-0019-Y | TENNETGMBH |  |  | 812 | 380 | 220 | 0.421 | 45.936 | -0.304 | 0.506 |  |  |  | 1.111
TR Audorf/S T421 | 11TD2T0000000142 | TENNETGMBH |  |  | 812 | 380 | 220 | 0.485 | 46.611 | -0.615 | 0.492 |  |  |  | 1.111
TR Bechterdissen T424 | 11TD2T000000246I | TENNETGMBH |  |  | 693 | 380 | 220 | 0.794 | 61.035 | -0.626 | 0.812 |  |  |  | 1.231
TR Bechterdissen T423 | 11TD2T000000245K | TENNETGMBH |  |  | 693 | 380 | 220 | 0.792 | 61.035 | -0.502 | 0.894 |  |  |  | 1.231
TR Bergrheinfeld VK5 | 11TD2T000000025Y | TENNETGMBH |  |  | 938 | 380 | 220 | 0.71 | 51.408 | -1.561 | 1.038 |  |  |  | 1.231
TR Brunsbuettel T421 | 11TD2T0000002013 | TENNETGMBH |  |  | 812 | 380 | 220 | 0.42 | 46.007 | -2.194 | 0.5 |  |  |  | 1.111
TR Buettel T441 | 11TD2T000000208Q | TENNETGMBH |  |  | 2061 | 380 | 220 | 0.579 | 58.424 | -2.032 | 1.174 |  |  |  | 1
TR Buettel T442 | 11TD2T000000209O | TENNETGMBH |  |  | 2061 | 380 | 220 | 0.577 | 58.386 | -1.9 | 1.19 |  |  |  | 1
TR Conneforde/O T422 | 11TD2T000000033Z | TENNETGMBH |  |  | 631 | 380 | 220 | 1.008 | 65.364 | -0.508 | 0.739 |  |  |  | 1.231
TR Conneforde/O T421 | 11TD2T0000002021 | TENNETGMBH |  |  | 1057 | 380 | 220 | 0.408 | 24.239 | -6.876 | 1.375 |  |  |  | 1.385
TR Conneforde/O T423 | 11T0-0000-1608-5 | TENNETGMBH |  |  | 812 | 380 | 220 | 0.414 | 45.9 | -7.973 | 0.484 |  |  |  | 1.111
PST Diele T441 | 11TD2T000000035V | TENNETGMBH |  |  | 1856 | 380 | 380 | 0.112 | 12.319 | -2.444 | 0.957 | -10;10 | 90 | Symmetrical |  | 1.271 | Connected to the line "Conneforde - Diele rot" (EIC: 11TD2L0000000471)
PST Diele T442 | 11TD2T000000036T | TENNETGMBH |  |  | 1856 | 380 | 380 | 0.111 | 12.319 | -2.453 | 0.935 | -10;10 | 90 | Symmetrical |  | 1.271 | Connected to the line "Conneforde - Diele weiss" (EIC: 11TD2L000000049Y)
TR Diele T1 | 11TD2T000000219L | TENNETGMBH |  |  | 4461 | 380 | 220 | 0.745 | 46.529 | -0.62 | 0.928 |  |  |  | 1.5
TR Doerpen/W T441 | 11TD2T000000229I | TENNETGMBH |  |  | 1734 | 380 | 380 | 0.612 | 42.189 | -0.678 | 1.179 |  |  |  | 1.25
TR Doerpen/W T442 | 11TD2T000000230X | TENNETGMBH |  |  | 1734 | 380 | 380 | 0.612 | 42.189 | -0.674 | 1.181 |  |  |  | 1.25
TR Doerpen/W T425 | 11T0-0000-1578-J | TENNETGMBH |  |  | 9999 | 380 | 380 | 0.43 | 45.206 | -0.98 | 1.723 |  |  |  | 1.1
TR Doerpen/W T426 | 11T0-0000-1579-G | TENNETGMBH |  |  | 9999 | 380 | 380 | 0.427 | 45.184 | -0.908 | 1.711 |  |  |  | 1.1
TR Doerpen/W T443 | 11TD2T000000227M | TENNETGMBH |  |  | 1955 | 380 | 380 | 0.602 | 42.978 | -0.816 | 1.158 |  |  |  | 1.25
TR Doerpen/W T444 | 11TD2T000000228K | TENNETGMBH |  |  | 1955 | 380 | 380 | 0.602 | 42.978 | -0.631 | 1.177 |  |  |  | 1.25
TR Dollern T422 | 11TD2T000000204Y | TENNETGMBH |  |  | 924 | 380 | 220 | 0.496 | 24.237 | -12.276 | 1.563 |  |  |  | 1.385
TR Dollern T421 | 11TD2T000000044U | TENNETGMBH |  |  | 935 | 380 | 220 | 0.642 | 51.196 | -5.241 | 2.044 |  |  |  | 1.4
TR Emden/O T428 | 11T0-0000-1589-C | TENNETGMBH |  |  | 812 | 380 | 220 | 0.416 | 45.865 | -4.306 | 0.47 |  |  |  | 1.111
TR Emden/O T425 | 11T0-0000-0070-0 | TENNETGMBH |  |  | 812 | 380 | 220 | 0.424 | 45.616 | -0.318 | 0.498 |  |  |  | 1.111
TR Etzenricht T421 | 11TD2T000000260O | TENNETGMBH |  |  | 811 | 380 | 220 | 0.518 | 47.002 | -0.444 | 0.545 |  |  |  | 1.111
TR Grosskrotzenburg T422 | 11TD2T000000071R | TENNETGMBH |  |  | 528 | 380 | 220 | 1.222 | 59.139 | -9.542 | 1.706 |  |  |  | 2
TR Grosskrotzenburg T423 | 11TD2T000000072P | TENNETGMBH |  |  | 1019 | 380 | 220 | 0.708 | 51.462 | -6.817 | 1.941 |  |  |  | 1.385
TR Grosskrotzenburg T421 | 11TD2T000000070T | TENNETGMBH |  |  | 1019 | 380 | 220 | 0.71 | 51.195 | -4.882 | 1.931 |  |  |  | 1.385
TR Irsching VK6 | 11TD2T000000096B | TENNETGMBH |  |  | 866 | 380 | 220 | 0.72 | 51.515 | -1.298 | 1.353 |  |  |  | 1.231
TR Landesbergen T422 | 11TD2T000000116V | TENNETGMBH |  |  | 974 | 380 | 220 | 0.658 | 49.862 | -8.033 | 1.881 |  |  |  | 1.385
TR Landesbergen T423 | 11TD2T000000117T | TENNETGMBH |  |  | 524 | 380 | 220 | 1.105 | 65.445 | -5.067 | 1.756 |  |  |  | 2.022
TR Oberbachern T421 | 11TD2T000000143S | TENNETGMBH |  |  | 923 | 380 | 220 | 0.636 | 49.169 | -3.64 | 1.941 |  |  |  | 1.231
TR Ottenhofen VK6 | 11TD2T000000146M | TENNETGMBH |  |  | 917 | 380 | 220 | 0.669 | 49.462 | -4.931 | 1.803 |  |  |  | 1.231
TR Ottenhofen VK7 | 11TD2T000000147K | TENNETGMBH |  |  | 952 | 380 | 220 | 0.668 | 49.195 | -6.829 | 2.031 |  |  |  | 1.231
TR Pleinting VK6 | 11TD2T000000155L | TENNETGMBH |  |  | 952 | 380 | 220 | 0.592 | 47.836 | -5.667 | 1.971 |  |  |  | 1.25
TR Pleinting VK7 | 11TD2T000000156J | TENNETGMBH |  |  | 952 | 380 | 220 | 0.664 | 48.849 | -6.468 | 1.931 |  |  |  | 1.231
TR Raitersaich VK6 | 11TD2T000000160S | TENNETGMBH |  |  | 926 | 380 | 220 | 0.684 | 50.369 | -2.139 | 1.522 |  |  |  | 1.245
TR Schwandorf VK5 | 11TD2T000000168C | TENNETGMBH |  |  | 935 | 380 | 220 | 0.617 | 49.329 | -5.201 | 2.143 |  |  |  | 1.231
TR Siems T421 | 11TD2T000000172L | TENNETGMBH |  |  | 559 | 380 | 220 | 1.072 | 86.439 | -0.741 | 0.648 |  |  |  | 1.231
TR Sottrum T421 | 11TD2T000000180M | TENNETGMBH |  |  | 649 | 380 | 220 | 0.486 | 46.824 | -0.573 | 0.498 |  |  |  | 1.111
TR Unterweser T421 | 11TD2T000000206U | TENNETGMBH |  |  | 1048 | 380 | 220 | 0.511 | 23.995 | -3.843 | 1.5 |  |  |  | 1.385
TR Wahle T421 | 11TD2T000000191H | TENNETGMBH |  |  | 952 | 380 | 220 | 0.712 | 49.862 | -3.899 | 1.753 |  |  |  | 1.385
TR Wahle T422 | 11TD2T000000192F | TENNETGMBH |  |  | 935 | 380 | 220 | 0.619 | 52.263 | -4.916 | 1.844 |  |  |  | 1.4
TR Wuergassen T421 | 11TD2T0000001975 | TENNETGMBH |  |  | 509 | 380 | 220 | 1.324 | 60.592 | -12.824 | 1.819 |  |  |  | 2.011
TR Wuergassen T422 | 11TD2T0000001983 | TENNETGMBH |  |  | 509 | 380 | 220 | 1.371 | 60.591 | -13.508 | 1.681 |  |  |  | 2.011
TR/ 380-220kV / Buers / Trafo 31 | 11T0-0000-0091-Q | TRANSNETBW |  |  | 879 | 220 | 380 | 0.3191 | 26.841 | -9.4368 | 2.3535 |  | 0 | Symmetrical | 1.154
TR / 380-220kV / Buers / Trafo 32 | 11T0-0000-0092-N | TRANSNETBW |  |  | 879 | 220 | 380 | 0.3174 | 26.902 | -10.8694 | 2.3251 |  | 0 | Symmetrical | 1.154
TR / 380-220kV / Buers / Trafo 33 | 11T0-0000-0093-K | TRANSNETBW |  |  | 879 | 220 | 380 | 0.3714 | 26.296 | -6.9725 | 2.3062 |  | 0 | Symmetrical | 1.154
TR / 380-220kV / Buers / Trafo 34 | 11T0-0000-0094-H | TRANSNETBW |  |  | 879 | 220 | 380 | 0.3839 | 26.19 | -7.7605 | 1.966 |  | 0 | Symmetrical | 1.154
TR / 380-220kV / Daxlanden / Trafo 401 | 11TD400000023-T9 | TRANSNETBW |  |  | 1443 | 380 | 220 | 0.24722 | 24.639 | -2.265 | 1.0581 |  | 0 | Symmetrical | 1.389
TR / 380-220kV / Daxlanden / Trafo 402 | 11TD400000028-TQ | TRANSNETBW |  |  | 1443 | 380 | 220 | 0.34336 | 24.158 | -7.5816 | 1.6069 |  | 0 | Symmetrical | 1.444
TR / 380-220kV / Eichstetten / Trafo 401 | 11TD400000041-T7 | TRANSNETBW |  |  | 1443 | 380 | 220 | 0.24368 | 24.367 | -2.0484 | 1.0731 |  | 0 | Symmetrical | 1.389
TR / 380-220kV / Kuehmoos Trafo 401 | 12T-0000000591-H | TRANSNETBW |  |  | 953 | 380 | 220 | 0.4011 | 24.482 | -10.6436 | 1.3187 | -3;3 | -120 | Asymmetrical | 1.385
TR / 380-220kV / Neurott / Trafo 401 | 11TD400000125-TW | TRANSNETBW |  |  | 1506 | 220 | 380 | 0.19433 | 16.618 | -6.9137 | 4.5558 |  | 0 | Symmetrical | 1.231
TR / 380-220kV / Neurott / Trafo 402 | 11TD400000127-TO | TRANSNETBW |  |  | 953 | 380 | 220 | 0.7077 | 24.242 | -3.2286 | 1.47 |  | 0 | Symmetrical | 1.385
PST / 380-220kV / Buers / Trafo 37 | 11T0-0000-0082-R | TRANSNETBW |  |  | 1106 | 380 | 220 | 0.2149 | 19.315 | -11.2148 | 3.4513 | -17;17 | 90 | Asymmetrical | 1.14 | 1.794 | Connected in substation Bürs
TR / 380-220kV / Pulverdingen / Trafo 323 | 11TD400000144-TQ | TRANSNETBW |  |  | 1506 | 220 | 380 | 0.18397 | 10.226 | -2.089 | 1.9168 |  | 0 | Symmetrical | 1.231
TR / 380-220kV / Wendlingen / Trafo 324 | 11TD400000184-T6 | TRANSNETBW |  |  | 762 | 220 | 380 | 0.40299 | 26.145 | -2.7067 | 2.702 |  | 0 | Symmetrical | 1.154

## Remedial Actions
Location
Name of RA | TSO | Description
PST_Roehrsdorf_441 | 50HERTZ | Change of tap position of phase shifting transformer (380/220) in 400 kV substation Roehrsdorf
PST_Roehrsdorf_442 | 50HERTZ | Change of tap position of phase shifting transformer (380/220) in 400 kV substation Roehrsdorf
PST_Vierraden_441 | 50HERTZ | Change of tap position of phase shifting transformer (380/220) in 400 kV substation Vierraden
PST_Vierraden_443 | 50HERTZ | Change of tap position of phase shifting transformer (380/220) in 400 kV substation Vierraden
PST_Gronau | Amprion GmbH | PST as preventive RA. Provided range of taps [-10; 10]
PST_EHPST | APG | Change of tap position of phase shifting transformer (220/220) in 220kV substation Ernsthofen
PST_TAPST | APG | Change of tap position of phase shifting transformer (220/220) in 220kV substation Tauern
PST_TEPST | APG | Change of tap position of phase shifting transformer (220/220) in 220kV substation Ternitz
TOP_SPCPL1 | APG | Opening of busbar coupler in 380kV substation St. Peter (Normal operation: one-node operation)
PST_CHRD_1 | CEPS | Change of tap position of phase shifting transformer in 380kV substation Hradec
PST_CHRD_2 | CEPS | Change of tap position of phase shifting transformer in 380kV substation Hradec
PST_CHRD_3 | CEPS | Change of tap position of phase shifting transformer in 380kV substation Hradec
PST_CHRD_4 | CEPS | Change of tap position of phase shifting transformer in 380kV substation Hradec
TOP_OPEN_Nosovice | CEPS | Opening of busbar coupler in 380kV substation Nosovice (Normal operation: one-node)
TOP_OPEN_C. Stred 1 | CEPS | Opening of busbar coupler in 380kV substation C. Stred (Normal operation: one-node)
TOP_OPEN_C. Stred 2 | CEPS | Opening of busbar coupler in 220kV substation C. Stred (Normal operation: one-node)
TOP_OPEN_Sokolnice | CEPS | Opening of busbar coupler in 220kV substation Sokolnice (Normal operation: one-node)
TOP_OPEN_Liskovec | CEPS | Opening of busbar coupler in 220kV substation Liskovec (Normal operation: one-node)
TOP_OPEN_Prosenice | CEPS | Opening of busbar coupler in 220kV substation Prosenice (Normal operation: one-node)
TOP_2N_PODLOG_CRA | ELES | Opening of busbar coupler in 220kV substation Podlog (Normal operation: one-node)
TOP_2N_PODLOG_PRA | ELES | Opening of busbar coupler in 220kV substation Podlog (Normal operation: one-node)
PST_VANYK D1_CRA | ELIA | Curatively change of tap position of phase shifting transformer 1 (380/380) in 380kV substation Van Eyck
PST_VANYK D2_CRA | ELIA | Curatively change of tap position of phase shifting transformer 2 (380/380) in 380kV substation Van Eyck
PST_ZANDV D1_CRA | ELIA | Curatively change of tap position of phase shifting transformer 1 (380/380) in 380kV substation Zandvliet
PST_ZANDV D2_CRA | ELIA | Curatively change of tap position of phase shifting transformer 2 (380/380) in 380kV substation Zandvliet
PST_VANYK D1_PRA | ELIA | Preventively change of tap position of phase shifting transformer 1 (380/380) in 380kV substation Van Eyck
PST_VANYK D2_PRA | ELIA | Preventively change of tap position of phase shifting transformer 2 (380/380) in 380kV substation Van Eyck
PST_ZANDV D1_PRA | ELIA | Preventively change of tap position of phase shifting transformer 1 (380/380) in 380kV substation Zandvliet
PST_ZANDV D2_PRA | ELIA | Preventively change of tap position of phase shifting transformer 2 (380/380) in 380kV substation Zandvliet
PST_ZANDV DA_PRA | ELIA | Preventively equal change of tap position of both phase shifting transformers (380/380) in 380kV substation Zandvliet
PST_ZANDV DA_PRA | ELIA | Preventively equal change of tap position of both phase shifting transformers (380/380) in 380kV substation Zandvliet
PST_ZANDV DA_CRA | ELIA | Curatively equal change of tap position of both phase shifting transformers (380/380) in 380kV substation Zandvliet
PST_ZANDV DA_CRA | ELIA | Curatively equal change of tap position of both phase shifting transformers (380/380) in 380kV substation Zandvliet
TOP_2N_AVLGM_CRA | ELIA | Curatively operate with 2 nodes in substation Avelgem
TOP_2N_COURC_CRA | ELIA | Curatively operate with 2 nodes in substation Courcelles
TOP_2N_HORTA_CRA | ELIA | Curatively operate with 2 nodes in substation Horta
TOP_2N_AVLGM_PRA | ELIA | Preventively operate with 2 nodes in substation Avelgem
TOP_2N_DOEL_PRA | ELIA | Preventively operate with 2 nodes in substation Doel
TOP_2N_BRUEG_CRA | ELIA | Curatively operate with 2 nodes in substation Bruegel
TOP_2N_COURC_PRA | ELIA | Preventively operate with 2 nodes in substation Courcelles
TOP_2N_BRUEG_PRA | ELIA | Preventively operate with 2 nodes in substation Bruegel
TOP_OPEN_AUBAN_BRUME_13_CRA | ELIA | Curatively take the line 380.13 Aubange-Brume out of service
TOP_2N_AUBAN_PRA | ELIA | Preventively operate with 2 nodes in substation Aubange
TOP_2N_AUBAN_CRA | ELIA | Curatively operate with 2 nodes in substation Aubange
TOP_1N_AVLGM_CRA | ELIA | Curatively operate with 1 nodes in substation Avelgem
TOP_1N_COURC_CRA | ELIA | Curatively operate with 1 nodes in substation Courcelles
TOP_1N_HORTA_CRA | ELIA | Curatively operate with 1 node in substation Horta
TOP_COMPLEX_GYOR_SZHO_ZURN_CRA | MAVIR | Opening of busbar couper in 400kV substation Gyor (complex case: multiple node operation)
TOP_COMPLEX_GYOR_SZHO_GABC_CRA | MAVIR | Opening of busbar couper in 400kV substation Gyor (complex case: multiple node operation)
TOP_COMPLEX_GYOR_LITR_GABC_CRA | MAVIR | Opening of busbar couper in 400kV substation Gyor (complex case: multiple node operation)
TOP_COMPLEX_GOD_AISA_LEVIC_CRA | MAVIR | Opening of busbar couper in 400kV substation God (complex case: multiple node operation)
TOP_COMPLEX_GOD_SAJO_LEVIC_CRA | MAVIR | Opening of busbar couper in 400kV substation God (complex case: multiple node operation)
TOP_COMPLEX_GONY_GYOR_GABC_CRA | MAVIR | Opening of busbar couper in 400kV substation Gonyu (complex case: multiple node operation)
TOP_COMPLEX_GONY_BICSD_VDUR_CRA | MAVIR | Opening of busbar couper in 400kV substation Gonyu (complex case: multiple node operation)
TOP_COMPLEX_GONY_GYOR_GABC_VDUR_CRA | MAVIR | Opening of busbar couper in 400kV substation Gonyu (complex case: multiple node operation)
PST MIKULOWA-PF1 | PSE | Change of tap position of phase shifting transformer (400) on line Mikulowa-Hagenwerder
PST MIKULOWA-PF2 | PSE | Change of tap position of phase shifting transformer (400) on line Mikulowa-Hagenwerder
PST MIKULOWA-PF3 | PSE | Change of tap position of phase shifting transformer (400) on line Mikulowa-Hagenwerder
PST MIKULOWA-PF4 | PSE | Change of tap position of phase shifting transformer (400) on line Mikulowa-Hagenwerder
PST MIKULOWA-TD1 | PSE | Change of tap position of phase shifting transformer (400/220) in substation Mikulowa
PST MIKULOWA-TD2 | PSE | Change of tap position of phase shifting transformer (400/220) in substation Mikulowa
PST JOACHIMOW-TD1 | PSE | Change of tap position of phase shifting transformer (400/220) in substation Joachimow
PST JOACHIMOW-TD2 | PSE | Change of tap position of phase shifting transformer (400/220) in substation Joachimow
PST GRUDZIADZ-A3 | PSE | Change of tap position of phase shifting transformer (400/220) in substation Grudziadz
TOP_COMPLEX_AVELIN_quarterbar1B_CRA | RTE | Opening of busbar coupler in 400kV substation Avelin (Normal operation: one-node) after contingency
TOP_COMPLEX_MERY_quarterbar1A_CRA | RTE | Opening of busbar coupler in 400kV substation Mery (Normal operation: one-node) after contingency
TOP_COMPLEX_2N_Moulaine225_OPEN_AT761_CRA | RTE | Opening of AT coupler in 225kV substation Moulaine (Normal operation: one-node) after contingency
TOP_2N_VIGY_tronconnement_CRA | RTE | Opening of busbar coupler in 400kV substation Vigy (Normal operation: one-node) after contingency
TOP_2N_VIGY_tronconnement_PRA | RTE | Opening of busbar coupler in 400kV substation Vigy (Normal operation: one-node)
TOP_COMPLEX_AVELIN_quarterbar3B_CRA | RTE | Opening of busbar coupler in 400kV substation Avelin (Normal operation: one-node) after contingency
TOP_2N_BEZAUMONT_CRA | RTE | Opening of busbar coupler in 400kV substation Bezaumont (Normal operation: one-node) after contingency
TOP_2N_CHEVALET_CRA | RTE | Opening of busbar coupler in 400kV substation Chevalet (Normal operation: one-node) after contingency
TOP_COMPLEX_2N_Moulaine225_OPEN_AT762_CRA | RTE | Opening of AT coupler in 225kV substation Moulaine (Normal operation: one-node) after contingency
TOP_COMPLEX_AVELIN_quarterbar2B_CRA | RTE | Opening of busbar coupler in 400kV substation Avelin (Normal operation: one-node) after contingency
TOP_OPEN_Chooz_Monceau_225_CRA | RTE | Opening of coupler in 225kV line Chooz Monceau after contingency
TOP_2N_AVELIN_tronconnement_CRA | RTE | Opening of busbar coupler in 400kV substation Avelin (Normal operation: one-node) after contingency
TOP_2N_AVELIN_tronconnement_PRA | RTE | Opening of busbar coupler in 400kV substation Avelin (Normal operation: one-node)
TOP_COMPLEX_LONNY_quarterbar1B_CRA | RTE | Opening of busbar coupler in 400kV substation Lonny (Normal operation: one-node) after contingency
TOP_OPEN_Mazures_AT_CRA | RTE | Opening of AT coupler in 225kV substation Mazures (Normal operation: one-node) after contingency
TOP_COMPLEX_2N_AVELIN_couplage_OPEN_AT762_CRA | RTE | Opening of AT coupler in 225kV substation Avelin (Normal operation: one-node) after contingency
TOP_COMPLEX_MASTAING_quarterbar1B_CRA | RTE | Opening of busbar coupler in 400kV substation Mastaing (Normal operation: one-node) after contingency
TOP_COMPLEX_MASTAING_quarterbar1B_PRA | RTE | Opening of busbar coupler in 400kV substation Mastaing (Normal operation: one-node)
TOP_COMPLEX_VIGY_quarterbar1B_CRA | RTE | Opening of busbar coupler in 400kV substation Vigy (Normal operation: one-node) after contingency
TOP_COMPLEX_MERY_quarterbar2A_CRA | RTE | Opening of busbar coupler in 400kV substation Mery (Normal operation: one-node) after contingency
TOP_OPEN_MUHLBACH_SCHEER_CRA | RTE | Opening of coupler in 400kV line Muhlbach Scheer after contingency
TOP_2N_LONNY_tronconnement_CRA | RTE | Opening of busbar coupler in 400kV substation Lonny (Normal operation: one-node) after contingency
TOP_2N_LONNY_tronconnement_PRA | RTE | Opening of busbar coupler in 400kV substation Lonny (Normal operation: one-node)
TOP_COMPLEX_MASTAING_quarterbar2B_CRA | RTE | Opening of busbar coupler in 400kV substation Mastaing (Normal operation: one-node) after contingency
TOP_COMPLEX_MASTAING_quarterbar2B_PRA | RTE | Opening of busbar coupler in 400kV substation Mastaing (Normal operation: one-node)
TOP_2N_MERY_tronconnement_CRA | RTE | Opening of busbar coupler in 400kV substation Mery (Normal operation: one-node) after contingency
TOP_OPEN_Capelle_AT_CRA | RTE | Opening of AT coupler in 225kV substation Capelle (Normal operation: one-node) after contingency
TOP_OPEN_Vola _V.Kapusany | SEPS | Switch off the line Vola - V. Kapusany
TOP_OPEN_Gabcikovo_P.Biskupice | SEPS | Switch off the line Gabcikovo - P. Biskupice
TOP_OPEN_Sucany_Varin | SEPS | Switch off the line Sucany - Varin
PST_ARAD_400/220_3 | TEL | Change of tap position of phase shifting transformer (400/220) in 400kV substation Arad
PST_URECHESTI_400/220_1 | TEL | Change of tap position of phase shifting transformer (400/220) in 400kV substation Urechesti
TOP_CLOSE_TR_MINTIA_400/220_3 | TEL | Connecting the second 400/220 kV transformer in substation Mintia (Normal operation: one transformer)
TOP_2N_Lelystad | TENNET NL | Opening of busbar coupler in 380kV substation Lelystad (Normal operation: one-node)
TOP_2N_Ens | TENNET NL | Opening of busbar coupler in 380kV substation Ens (Normal operation: one-node)
TOP_2N_Doetinchem | TENNET NL | Opening of busbar coupler in 380kV substation Doetinchem (Normal operation: one-node)
TOP_2N_Hengelo | TENNET NL | Opening of busbar coupler in 380kV substation Hengelo (Normal operation: one-node)
TOP_2N_Geertruidenberg | TENNET NL | Opening of busbar coupler in 380kV substation Geertruidenberg (Normal operation: one-node)
TOP_2N_Diemen | TENNET NL | Opening of busbar coupler in 380kV substation Diemen (Normal operation: one-node)
TOP_2N_Eindhoven | TENNET NL | Opening of busbar coupler in 380kV substation Eindhoven (Normal operation: one-node)
TOP_2N_Zwolle | TENNET NL | Opening of busbar coupler in 380kV substation Zwolle (Normal operation: one-node)
TOP_2N_1_Maasbracht | TENNET NL | Opening of busbar coupler 1 in 380kV substation Maasbracht (Normal operation: one-node)
TOP_2N_2_Maasbracht | TENNET NL | Opening of busbar coupler 2 in 380kV substation Maasbracht (Normal operation: one-node)
TOP_2N_Krimpen | TENNET NL | Opening of busbar coupler in 380kV substation Krimpen a/d IJssel (Normal operation: one-node)
TOP_2N_Rilland | TENNET NL | Opening of busbar coupler in 380kV substation Rilland (Normal operation: one-node)
PST_Meeden_W | TENNET NL | Change of tap position of phase shifting transformer in 380kV substation Meeden
PST_Meeden_Z | TENNET NL | Change of tap position of phase shifting transformer in 380kV substation Meeden
TOP_2N_GRAFENRHEINFELD_BERGRHEINFELD | TENNETGMBH | Opening of busbar coupler in 400kV substation Grafenrheinfeld/Bergrheinfeld (standard case: one node operation)
TOP_2N_DOERPENWEST | TENNETGMBH | Opening of busbar coupler in 400kV substation Doerpen West (standard case: one node operation)
TOP_2N_PLEINTING | TENNETGMBH | Opening of busbar coupler in 400kV substation Pleinting (standard case: one node operation)
TOP_2N_SITTLING | TENNETGMBH | Opening of busbar coupler in 220kV substation Sittling (standard case: one node operation)
PST_DIEL_T441 | TENNETGMBH | Change tap position of phase shifting transformer (380/380) in 400kV substation Diele
PST_DIEL_T442 | TENNETGMBH | Change tap position of phase shifting transformer (380/380) in 400kV substation Diele
TOP_2N_DELLMENSINGEN | TRANSNETBW | Opening of busbar coupler in 400kV substation Dellmensingen (Normal operation: one-node)
TOP_2N_EICHSTETTEN | TRANSNETBW | Opening of busbar coupler in 400kV substation Eichstetten (Normal operation: one-node operation)
PST_BUERS_BMT37 | TRANSNETBW | Change of tap position of phase shifting transformer (400/220) in 400kV substation Buers
TR_KUEHMOSS_BMT401 | TRANSNETBW | Change of tap position of transformer (400/220) in 400kV substation Kühmoos